## CR-SR Matrix
# | FR | Row Type | Component Display ID | Component Official ID | Component Type | Component Title | Component Requirement Text | Component Rationale and Supplemental Guidance | Component Security Levels | System Display ID | System Official ID | System Title | System Requirement Text | System Rationale and Supplemental Guidance | System Security Levels | Mapping Basis
1 | 1 | Base requirement | CR1.1 | CR 1.1 | CR | Human user identification and authentication | Component s shall provide the capability to identify and authenticate all human users according to IEC 62443 ‑3‑3 SR 1.1 on all interfaces capable of human user access. This capability shall enforce such identification and authentication on all interfaces that provide human user access to the component to support segregation of duties and least privilege in accordance with applicable security policies and procedures. This ca pability may be provided locally by the component or by integration into a system level identification and authentication system. NOTE Applicable security policies are a local matter. | All human users need to be identified and authenticated for all access to the component. Authentication of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or physically keyed lids, and in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of the authentication process. This requirement should be applied to both local and remote access to the component. This requirement comes in addition to the requirement of having such an authentication and identification at the system level. Interfaces capable of human user access are local user inter faces such as touchscreens, push buttons, keyboards, as well as network protocols designed for human user interactions such as hypertext transfer protocol (HTTP), HTTP secure (HTTPS), file transfer protocol (FTP), secure FTP (SFTP), protocols used for device configuration tools (which are sometimes proprietary and other times use open protocols). User identification and authentication may be role- based or group- based (such as, for some component interfaces, several users may share the same identity). User identification and authentication should not hamper fast, local emergency actions. In order to support IAC policies, as defined according to IEC 62443 ‑2‑1 [1], the component should verif y the identity of all human users as a first step. In a second step, the permissions assigned to the identified human user should be enforced (see 6.3). | The requirements for the four security levels that relate to C R 1.1 are: • SL-C(IAC,component) 1: CR 1.1 • SL-C(IAC,component) 2: CR 1.1 (1) • SL-C(IAC,component) 3: CR 1.1 (1) (2) • SL-C(IAC,component) 4: CR 1.1 (1) (2) | SR1.1 | SR 1.1 | Human user identification and authentication | The control sys tem shall provide the capability to identify and authenticate all human users. This capability shall enforce such identification and authentication on all interfaces which provide human user access to the control system to support segregation of duties and least privilege in accordance with applicable security polic ies and procedures. | All human users need to be identified and authenticated for all access to the control system. Authentic ation of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or, in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of t he authentication process. This requirement should be applied to both local and remote access to the control system. In addition to identifying and authenticating all human users at the control system level (for example, at system logon), identification a nd authentication mechanisms are often employed at the application level. Where human users function as a single group (such as control room operators), user identification and authentication may be role -based or group- based. For some control system s, the c apability for immediate operator interaction is critical. It is essential that l ocal emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). Access to these systems may be restricted by appropriate physical security mechanisms (see IEC 62443‑2‑1). An example of such a situation is a critical operations room where strict physical access control and monitoring is in place and where shift plans allocate responsibility to a group of users. These users may then be using the same user identity. In addition, the designated operator workstation clients should be authenticated (see 5.4, SR 1.2 – Software process and device identification and authentication) or the use of this shared account should be limited to the constrained environment of the control room. In order to support IAC policies, as defined according to IEC 62443‑2‑1, the control system verif ies the identity of a ll human user s as a first step. In a second step, the permissions assigned to the identified human user are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.1 – Human user identification and authentication are: • SL-C(IAC, control system) 1: SR 1.1 • SL-C(IAC, control system) 2: SR 1.1 (1) • SL-C(IAC, control system) 3: SR 1.1 (1) (2) • SL-C(IAC, control system) 4: SR 1.1 (1) (2) (3) | Same base identifier and enhancement sequence
2 | 1 | Enhancement | CR1.1.1 | CR 1.1 RE (1) | CR | Unique identification and authentication | Component s shall provide the capability to uniquely identify and authenticate all human users. | All human users need to be identified and authenticated for all access to the component. Authentication of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or physically keyed lids, and in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of the authentication process. This requirement should be applied to both local and remote access to the component. This requirement comes in addition to the requirement of having such an authentication and identification at the system level. Interfaces capable of human user access are local user inter faces such as touchscreens, push buttons, keyboards, as well as network protocols designed for human user interactions such as hypertext transfer protocol (HTTP), HTTP secure (HTTPS), file transfer protocol (FTP), secure FTP (SFTP), protocols used for device configuration tools (which are sometimes proprietary and other times use open protocols). User identification and authentication may be role- based or group- based (such as, for some component interfaces, several users may share the same identity). User identification and authentication should not hamper fast, local emergency actions. In order to support IAC policies, as defined according to IEC 62443 ‑2‑1 [1], the component should verif y the identity of all human users as a first step. In a second step, the permissions assigned to the identified human user should be enforced (see 6.3). | The requirements for the four security levels that relate to C R 1.1 are: • SL-C(IAC,component) 1: CR 1.1 • SL-C(IAC,component) 2: CR 1.1 (1) • SL-C(IAC,component) 3: CR 1.1 (1) (2) • SL-C(IAC,component) 4: CR 1.1 (1) (2) | SR1.1.1 | SR 1.1 RE (1) | Unique identification and authentication | The control system shall provide the capability to uniquely identify and authenticate all human users. | All human users need to be identified and authenticated for all access to the control system. Authentic ation of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or, in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of t he authentication process. This requirement should be applied to both local and remote access to the control system. In addition to identifying and authenticating all human users at the control system level (for example, at system logon), identification a nd authentication mechanisms are often employed at the application level. Where human users function as a single group (such as control room operators), user identification and authentication may be role -based or group- based. For some control system s, the c apability for immediate operator interaction is critical. It is essential that l ocal emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). Access to these systems may be restricted by appropriate physical security mechanisms (see IEC 62443‑2‑1). An example of such a situation is a critical operations room where strict physical access control and monitoring is in place and where shift plans allocate responsibility to a group of users. These users may then be using the same user identity. In addition, the designated operator workstation clients should be authenticated (see 5.4, SR 1.2 – Software process and device identification and authentication) or the use of this shared account should be limited to the constrained environment of the control room. In order to support IAC policies, as defined according to IEC 62443‑2‑1, the control system verif ies the identity of a ll human user s as a first step. In a second step, the permissions assigned to the identified human user are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.1 – Human user identification and authentication are: • SL-C(IAC, control system) 1: SR 1.1 • SL-C(IAC, control system) 2: SR 1.1 (1) • SL-C(IAC, control system) 3: SR 1.1 (1) (2) • SL-C(IAC, control system) 4: SR 1.1 (1) (2) (3) | Same base identifier and enhancement sequence
3 | 1 | Enhancement | CR1.1.2 | CR 1.1 RE (2) | CR | Multifactor authentication for all interfaces | Component s shall provide the capability to employ multifactor authentication for all human user access to the component. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | All human users need to be identified and authenticated for all access to the component. Authentication of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or physically keyed lids, and in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of the authentication process. This requirement should be applied to both local and remote access to the component. This requirement comes in addition to the requirement of having such an authentication and identification at the system level. Interfaces capable of human user access are local user inter faces such as touchscreens, push buttons, keyboards, as well as network protocols designed for human user interactions such as hypertext transfer protocol (HTTP), HTTP secure (HTTPS), file transfer protocol (FTP), secure FTP (SFTP), protocols used for device configuration tools (which are sometimes proprietary and other times use open protocols). User identification and authentication may be role- based or group- based (such as, for some component interfaces, several users may share the same identity). User identification and authentication should not hamper fast, local emergency actions. In order to support IAC policies, as defined according to IEC 62443 ‑2‑1 [1], the component should verif y the identity of all human users as a first step. In a second step, the permissions assigned to the identified human user should be enforced (see 6.3). | The requirements for the four security levels that relate to C R 1.1 are: • SL-C(IAC,component) 1: CR 1.1 • SL-C(IAC,component) 2: CR 1.1 (1) • SL-C(IAC,component) 3: CR 1.1 (1) (2) • SL-C(IAC,component) 4: CR 1.1 (1) (2) | SR1.1.2 | SR 1.1 RE (2) | Multifactor authentication for untrusted networks | The control system shall provide the capability to employ multifactor authentication for human user access to the control system via an untrusted network (see 5.15, SR 1.13 – Access via untrusted networks). NOTE See 5.7.3. 5.7.3.1, SR 1.5 – Authenticator management, RE 5.7.3.1 for enhanced authenticator management for software processes. | All human users need to be identified and authenticated for all access to the control system. Authentic ation of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or, in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of t he authentication process. This requirement should be applied to both local and remote access to the control system. In addition to identifying and authenticating all human users at the control system level (for example, at system logon), identification a nd authentication mechanisms are often employed at the application level. Where human users function as a single group (such as control room operators), user identification and authentication may be role -based or group- based. For some control system s, the c apability for immediate operator interaction is critical. It is essential that l ocal emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). Access to these systems may be restricted by appropriate physical security mechanisms (see IEC 62443‑2‑1). An example of such a situation is a critical operations room where strict physical access control and monitoring is in place and where shift plans allocate responsibility to a group of users. These users may then be using the same user identity. In addition, the designated operator workstation clients should be authenticated (see 5.4, SR 1.2 – Software process and device identification and authentication) or the use of this shared account should be limited to the constrained environment of the control room. In order to support IAC policies, as defined according to IEC 62443‑2‑1, the control system verif ies the identity of a ll human user s as a first step. In a second step, the permissions assigned to the identified human user are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.1 – Human user identification and authentication are: • SL-C(IAC, control system) 1: SR 1.1 • SL-C(IAC, control system) 2: SR 1.1 (1) • SL-C(IAC, control system) 3: SR 1.1 (1) (2) • SL-C(IAC, control system) 4: SR 1.1 (1) (2) (3) | Same base identifier and enhancement sequence
4 | 1 | Base requirement | CR1.2 | CR 1.2 | CR | Software process and device identification and authentication | Component s shall provide the capability to identify itself and authenticate to any other component (software application, embedded devices, host devices and network devices), accordi ng to IEC 62443 ‑3‑3 SR1.2. If the component, as in the case of an application, is running in the context of a human user, in addition, the identification and authentication of the human user according to IEC 62443 ‑3‑3 SR1.1 may be part of the component identification and authentication process towards the other components. | The function of identification and authentication is to map a known identity to an unknown software process or device (henceforth referred to as an entity in 5.4.2) so as to make it known before allowing any data exchange. Allowing rogue entities to send and receive control system specific data can result in detrimental behaviou r of the co ntrol system. All entities should be identified and authenticated for all access to the control system. Authentication of the identity of such entities should be accomplished by using methods such as passwords, tokens or location (physical or logical). This requirement should be applied to both local and remote access to the control system. However, in some scenarios where individual entities are used to connect to different target systems (for example, remote vendor support), it may be technically infeasi ble for an entity to have multiple identities. In these cases, compensating countermeasures would have to be applied. Special attention needs to be given when identifying and authenticating portable and mobile devices. These types of devices are a known method of introducing undesired network traffic, malware and/or information exposure to control systems, including otherwise isolated networks. Where entities function as a single group, identification and authentication may be role- based, group -based or entity -based. It is essential that local emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). For example, in common protection and control schemes, a group of devices jointly execute the protection functions and communicate with multicast messages among the devices in the group. In these cases, group authentication based on shared accounts or shared symmetric keys are commonly used. In order to support identification and authentication control policies as defined according to IEC 62443 ‑2‑1 [1], the control system verifies the identity of all entities as a first step. In a second step, the permissions assigned to the identified entity are enforced (see 6.3). | The requirements for the four security levels that relate to CR 1.2 are: • SL-C(IAC,component) 1: Not s elected • SL-C(IAC,component) 2: CR 1.2 • SL-C(IAC,component) 3: CR 1.2 (1) • SL-C(IAC,component) 4: CR 1.2 (1) | SR1.2 | SR 1.2 | Software process and device identification and authentication | The control system shall provide the capability to identify and authenticate all software processes and devices. This capability shall enforce such identification and authentication on all interfaces which provide access to the control system to support least privilege in accordance with applicable security policies and procedures. | The function of identification and authentication is to map an ID to an unknown software process or device (henceforth referred to an entity in this sub- clause) so as to make it known before allowing any data exchange. Allowing rogue entities to send and receive control system specific data can result in detrimental behavior of the legitimate control system. All entities need to be identified and authenticated for all access to the control system. Authentication of the identity of such entities should be accomplished by using methods such as passwords, tokens or location (physical or logical). This requirement should be applied to both local and remote access to the control system. However, in some scenarios where individual entities are used to conn ect to different target systems (for example, remote vendor support), it may be technical ly infeasible for an entity to have multiple identities. In these cases, compensating countermeasures would have to be applied. Identification and authentication mechanisms for all entities are needed to protect against attacks such as man- in-the-middle or message spoofing. In some cases, these mechanism s may involve multiple software processes running on the same physical server, each having their own identity. In other cases, the identity may be bound to the physical device, such as all processes running on a given PLC. Special attention needs to be made when identifying and authenticating portable and mobile devices. These types of devices are a known method of introducing undesired network traffic, malware and/or information exposure to control systems, including otherwise isolated networks. Where entities function as a single group, identification and authentication may be role -based, group -based or entity -based, i t is essential that local emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). For example, in common protection and control schemes, a group of devices jointly execute the protection functions and communicate with multicast messages among the devices in the group. In these cases, group authentication based on shared accounts or shared symmetric keys are commonly used. In order to support identification and authentication control policies as defined according to IEC 62443‑2‑1, the control system verifies the identity of all entities as a first step. In a second step, the permissions assigned to the identified entity are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.2 – Software process and device identification and authentication are: • SL-C(IAC, control system) 1: Not Selected • SL-C(IAC, control system) 2: SR 1.2 • SL-C(IAC, control system) 3: SR 1.2 (1) • SL-C(IAC, control system) 4: SR 1.2 (1) | Same base identifier and enhancement sequence
5 | 1 | Enhancement | CR1.2.1 | CR 1.2 RE (1) | CR | Unique identification and authentication | Component s shall provide the capability to uniquely identify and authenticate itself to any other component. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | The function of identification and authentication is to map a known identity to an unknown software process or device (henceforth referred to as an entity in 5.4.2) so as to make it known before allowing any data exchange. Allowing rogue entities to send and receive control system specific data can result in detrimental behaviou r of the co ntrol system. All entities should be identified and authenticated for all access to the control system. Authentication of the identity of such entities should be accomplished by using methods such as passwords, tokens or location (physical or logical). This requirement should be applied to both local and remote access to the control system. However, in some scenarios where individual entities are used to connect to different target systems (for example, remote vendor support), it may be technically infeasi ble for an entity to have multiple identities. In these cases, compensating countermeasures would have to be applied. Special attention needs to be given when identifying and authenticating portable and mobile devices. These types of devices are a known method of introducing undesired network traffic, malware and/or information exposure to control systems, including otherwise isolated networks. Where entities function as a single group, identification and authentication may be role- based, group -based or entity -based. It is essential that local emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). For example, in common protection and control schemes, a group of devices jointly execute the protection functions and communicate with multicast messages among the devices in the group. In these cases, group authentication based on shared accounts or shared symmetric keys are commonly used. In order to support identification and authentication control policies as defined according to IEC 62443 ‑2‑1 [1], the control system verifies the identity of all entities as a first step. In a second step, the permissions assigned to the identified entity are enforced (see 6.3). | The requirements for the four security levels that relate to CR 1.2 are: • SL-C(IAC,component) 1: Not s elected • SL-C(IAC,component) 2: CR 1.2 • SL-C(IAC,component) 3: CR 1.2 (1) • SL-C(IAC,component) 4: CR 1.2 (1) | SR1.2.1 | SR 1.2 RE (1) | Unique identification an d authentication | The control system shall provide the capability to uniquely identify and authenticate all software processes and devices. 5.4.3.2 Void | The function of identification and authentication is to map an ID to an unknown software process or device (henceforth referred to an entity in this sub- clause) so as to make it known before allowing any data exchange. Allowing rogue entities to send and receive control system specific data can result in detrimental behavior of the legitimate control system. All entities need to be identified and authenticated for all access to the control system. Authentication of the identity of such entities should be accomplished by using methods such as passwords, tokens or location (physical or logical). This requirement should be applied to both local and remote access to the control system. However, in some scenarios where individual entities are used to conn ect to different target systems (for example, remote vendor support), it may be technical ly infeasible for an entity to have multiple identities. In these cases, compensating countermeasures would have to be applied. Identification and authentication mechanisms for all entities are needed to protect against attacks such as man- in-the-middle or message spoofing. In some cases, these mechanism s may involve multiple software processes running on the same physical server, each having their own identity. In other cases, the identity may be bound to the physical device, such as all processes running on a given PLC. Special attention needs to be made when identifying and authenticating portable and mobile devices. These types of devices are a known method of introducing undesired network traffic, malware and/or information exposure to control systems, including otherwise isolated networks. Where entities function as a single group, identification and authentication may be role -based, group -based or entity -based, i t is essential that local emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). For example, in common protection and control schemes, a group of devices jointly execute the protection functions and communicate with multicast messages among the devices in the group. In these cases, group authentication based on shared accounts or shared symmetric keys are commonly used. In order to support identification and authentication control policies as defined according to IEC 62443‑2‑1, the control system verifies the identity of all entities as a first step. In a second step, the permissions assigned to the identified entity are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.2 – Software process and device identification and authentication are: • SL-C(IAC, control system) 1: Not Selected • SL-C(IAC, control system) 2: SR 1.2 • SL-C(IAC, control system) 3: SR 1.2 (1) • SL-C(IAC, control system) 4: SR 1.2 (1) | Same base identifier and enhancement sequence
6 | 1 | Base requirement | CR1.3 | CR 1.3 | CR | Account management | Component s shall provide the capability to support the management of all accounts directly or integrated into a system that manages accounts according to IE C 62443 ‑3‑3 SR 1.3. | A component may provide this capability by integrating into a higher -level account management system. If the capability is not integrated into a higher -level account management system then the component is expected to provide the capability natively. A common approach meeting this requirement would be a component that delegates the valuation of authentication to a directory server (for example, LDAP or Active Directory) which provides the account management capabilities required by IEC 62443 ‑3‑3 SR 1. 3. When a component integrates into a higher -level system to provide the account management capabilities there needs to be consideration for the impact to the component in the event that the higher -level system capability becomes unavailable. | The requirements for the four security levels that relate to CR 1.3 are: • SL-C(IAC,component) 1: CR 1.3 • SL-C(IAC,component) 2: CR 1.3 • SL-C(IAC,component) 3: CR 1.3 • SL-C(IAC,component) 4: CR 1.3 | SR1.3 | SR 1.3 | Account management | The control system shall provide the capability to support the management of all accounts by authorized users, including adding, a ctivating, modifying, disabling and removing accounts. | Account management may include grouping of accounts (for example, individual, role -based, device -based and control system), establishment of conditions for group membership and assignment of associated authorizations. In certain IACS instances, where individual accounts are determined to be unnecessary from a risk -analysis and/or regulatory aspect, shared accounts are acceptable as long as adequate compensating countermeasures (such as limited physical access or organizational measures for approval) are in place and documented. Non-human user accounts (sometimes termed service accounts) that are utilized for software process -to-process communication (for example, control server to historian and PLC to control server) typic ally require different security policies and procedures from human user accounts. For enhanced security, management of accounts should be done according to unified policies and deployed locally in the relevant components of the control system. Unused default system accounts used for the first installation of the system should be removable. Security enhancement lies in the simplification and consistent application of account management. | The requirements for the four SL levels that relate to SR 1.3 – Account management are: • SL-C(IAC, control system) 1: SR 1. 3 • SL-C(IAC, control system) 2: SR 1. 3 • SL-C(IAC, control system) 3: SR 1. 3 (1) • SL-C(IAC, control system) 4: SR 1. 3 (1) | Same base identifier and enhancement sequence
7 | 1 | Base requirement | CR1.4 | CR 1.4 | CR | Identifier management | Component s shall provide the capability to integrate into a system that supports the management of identifiers and/or provide the capability to support the management of identifiers directly according to IEC 62443 ‑3‑3 SR 1.4. | Accounts c reated under CR 1.3 – Account management (5.5) require the use of one or more identifiers to distinctly identify each account. These identifiers should be unique a nd unambiguous as to the account with which they are associated. Some examples of identifiers in common use are account names, UNIX user IDs, Microsoft Windows account globally unique identifiers (GUID), and bound X.509 certificates. A component may provid e a local © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 capability to associate identifiers with accounts. If the component is integrated into a system that enforces a system -wide security policy, it is highly recommended that identifiers be associated with the same account across all components in the system. In order to accomplish this, a component should be able to integrate into a system -wide identifier management capability. | The requirements for the four security levels that relate to CR 1.4 are: • SL-C(IAC,component) 1: CR 1.4 • SL-C(IAC,component) 2: CR 1.4 • SL-C(IAC,component) 3: CR 1.4 • SL-C(IAC,component) 4: CR 1.4 | SR1.4 | SR 1.4 | Identifier management | The control system shall provide the capability to support the management of identifiers by user, group, role or control system interface. | Identifiers are distinguished from the privileges which they permit an entity to perform within a specific control system control domain or zone (see 6.3, SR 2.1 – Authori zation enforcement). Where human users function as a single group (such as control room operators), user identification may be role -based, group- based or device- based. For some control sys tems, the capability for immediate operator interaction is critical. Local emergency actions for the control system should not be hampered by identification requirements. Access to these systems may be restricted by appropriate compensating countermeasures. Identifiers may be required on portions of the control system but not necessarily the entire control system. For example, wireless devices typically require identifiers, whereas wired devices may not. The management of identifiers will be determined by local policies and procedures established in compliance with IEC 62443‑2‑1. | The requirements for the four SL levels that relate to SR 1.4 – Identifier management are: • SL-C(IAC, control system) 1: SR 1. 4 • SL-C(IAC, control system) 2: SR 1. 4 • SL-C(IAC, control system) 3: SR 1. 4 • SL-C(IAC, control system) 4: SR 1. 4 | Same base identifier and enhancement sequence
8 | 1 | Base requirement | CR1.5 | CR 1.5 | CR | Authenticator management | Components shall provide the capability to: a) support the use of initial authenticator content; b) support the recognition of changes to default authenticators made at installation time; c) function properly with periodic authenticator change/refresh operation; and d) protect authenticators from unauthorized disclosure and modification when stored, used and t ransmitted. | In addition to an identifier (see 5.6) an authenticator is required to prove identity. Control system authenticator s include, but are not limited to, tokens, symmetric keys, private keys (part of a public/private key pair), biometrics, passwords, physical keys and key cards. There should be security policies in place instructing human users to take reasonable measures to safeguard authenticators, including maintaining possession of their individual authenticators, not loaning or sharing authenticators with others and reporting lost or compromised authenticators immediately. Authenticators have a lifecycle. When an accou nt is created automatically a new authenticator needs to be created, in order for the account owner to be able to authenticate. For example, in a password- based system, the account has a password associated with it. Definition of the initial authenticator content could be interpreted as the administrator defining the initial password that the account management system sets for all new accounts. Being able to configure these initial values makes it harder for an attacker to guess the password between account creation and first account use (which should involve the setting of a new password by the account owner). Some control systems are installed with unattended installers that create all necessary accounts with default passwords and some embedded devices are shipped with default passwords. Over time, these passwords often become general knowledge and are documented on the Internet. Being able to change the default passwords protects the system against unauthorized users using default passwords to gain access. Passwords can be obtained from storage or from transmission when used in network authentication. The complexity of this can be increased by cryptographic protections such as encryption or hashing or b y handshake protocols that do no t require transmission of the password at all. Still, passwords might be subject to attacks, for example, brute force guessing or breaking the cryptographic protection of passwords in transit or storage. The window of opportunity can be reduced by changing/refreshing the passwords periodically. Similar considerations apply to © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 authentication systems based on cryptographic keys. Enhanced protection can be achieved by using hardware mechanisms such as hardware security modules like trusted platform modules (TPMs). The m anagement of authenticators should be specified in applicable security policies and procedures, for example, constraints to change default authenticators, refresh periods, specification of the protection of authenticators or firecall procedures. Besides th e capabilities for authenticator management specified in this requirement, the strength of the authentication mechanism depends on the strength of the chosen authenticator (for example, password complexity or key length in public key authentication) and the policies for validating the authenticator in the authentication process (for example, how long a password is valid or which checks are performed in public key certificate validation). For the most common authentication mechanisms, password- based and publ ic key authentication, 5.9, 5.10 and 5.11 provide further requirements. Use of component s for some operations may be restricted, requiring addition al authentication (such as tokens, keys and certificates) in order to perform some funct ions. | The requirements for the four security levels that relate to CR 1.5 are: • SL-C(IAC,component) 1: CR 1.5 • SL-C(IAC,component) 2: CR 1.5 • SL-C(IAC,component) 3: CR 1.5 (1) • SL-C(IAC,component) 4: CR 1.5 (1) | SR1.5 | SR 1.5 | Authenticator management | The control system shall provide the capability to: h) initialize authenticator content; i) change all default authenticators upon control system installation; j) change/refresh all authenticators; and k) protect all authenticat ors from unauthorized disclosure and modification when stored and transmitte d. | In addition to an identifier (see 5.6, SR 1.4 – Identifier management) an authenticator is required to prove identity. Control system authenticators include, but are not limited to, tokens, symmetric keys, private keys (part of a public/private key pair), biometrics, passwords, physical keys and key cards. Human users should take reasonable measures to safeguard authenticators, including maintaining possession of their individual authenticators, not loaning or sharing authenticators with others and reporting lost or compromi sed authenticators immediately. Authenticators have a lifecycle. When an account is created automatically a new authenticator needs to be created, in order for the account owner to be able to authenticate. For example, in a password- based system, the account has a password associated with it. Definition of the initial authenticator content could be interpreted as the administrator defining the initial password which the account management system sets for all new accounts. Being able to configure these initial values makes it harder for an attacker to guess the password between account creation and first account use (which should involve t he setting of a new password by the account owner). Some control systems are installed with unattended installers which create all necessary accounts with default passwords and some embedded devices are shipped with default passwords. Over time, these pass words often become general knowledge and are documented on the Internet. Being able to change the default passwords protects the system against unauthorized users using default passwords to gain access. Passwords can be obtained from storage or from transm ission when used in network authentication. The complexity of this can be increased by cryptographic protections such as encryption or hashing or by handshake protocols which do no t require transmission of the password at all. Still, passwords might be subject to attacks, for example brute force guessing or breaking the cryptographic protection of passwords in transit or storage. The window of opportunity can be reduced by changing/refreshing the passwords periodically. Similar considerations apply to authentication systems based on cryptographic keys. Enhanced protection can be achieved by using hardware mechanisms such as hardware security modules like trusted platform modules (TPMs). The management of authenticators should be specified in applicable secur ity policies and procedures, for example, constraints to change default authenticators, refresh periods, specification of the protection of authenticators or firecall (see 3.1.24) procedures. Lockout or loss of control due to security measures is not acceptable. If the control system is required to have a high level of availability, measures should be taken to maintain this high level of availability (such as compensating ph ysical countermeasures, duplicate keys and supervisory override). Besides the capabilities for authenticator management specified in this requirement, the strength of the authentication mechanism depends on the strength of the chosen authenticator (for example password complexity or key length in public key authentication) and the policies for validating the authenticator in the authentication process (for example how long a password is valid or which checks are performed in public key certi ficate validation). For the most common authentication mechanisms password- based and public key authentication 5.9, SR 1.7 – Strength of passw ord-based authentication, 5.10, SR 1.8 – Public key infrastructure (PKI) c ertificates and 5.11, SR 1.9 – Strength of public key authentication provide further requirements. | The requirements for the four SL levels that relate to SR 1.5 – Authenticator management are: • SL-C(IAC, control system) 1: SR 1. 5 • SL-C(IAC, control system) 2: SR 1. 5 • SL-C(IAC, control system) 3: SR 1. 5 (1) • SL-C(IAC, control system) 4: SR 1. 5 (1) | Same base identifier and enhancement sequence
9 | 1 | Enhancement | CR1.5.1 | CR 1.5 RE (1) | CR | Hardware security for authenticators | The authenticators on which the component rely shall be protected via hardware mechanisms. EXAMPLE Password protected memory, OTP memory, hardware data integrity checks, and device security boot mechanism. | In addition to an identifier (see 5.6) an authenticator is required to prove identity. Control system authenticator s include, but are not limited to, tokens, symmetric keys, private keys (part of a public/private key pair), biometrics, passwords, physical keys and key cards. There should be security policies in place instructing human users to take reasonable measures to safeguard authenticators, including maintaining possession of their individual authenticators, not loaning or sharing authenticators with others and reporting lost or compromised authenticators immediately. Authenticators have a lifecycle. When an accou nt is created automatically a new authenticator needs to be created, in order for the account owner to be able to authenticate. For example, in a password- based system, the account has a password associated with it. Definition of the initial authenticator content could be interpreted as the administrator defining the initial password that the account management system sets for all new accounts. Being able to configure these initial values makes it harder for an attacker to guess the password between account creation and first account use (which should involve the setting of a new password by the account owner). Some control systems are installed with unattended installers that create all necessary accounts with default passwords and some embedded devices are shipped with default passwords. Over time, these passwords often become general knowledge and are documented on the Internet. Being able to change the default passwords protects the system against unauthorized users using default passwords to gain access. Passwords can be obtained from storage or from transmission when used in network authentication. The complexity of this can be increased by cryptographic protections such as encryption or hashing or b y handshake protocols that do no t require transmission of the password at all. Still, passwords might be subject to attacks, for example, brute force guessing or breaking the cryptographic protection of passwords in transit or storage. The window of opportunity can be reduced by changing/refreshing the passwords periodically. Similar considerations apply to © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 authentication systems based on cryptographic keys. Enhanced protection can be achieved by using hardware mechanisms such as hardware security modules like trusted platform modules (TPMs). The m anagement of authenticators should be specified in applicable security policies and procedures, for example, constraints to change default authenticators, refresh periods, specification of the protection of authenticators or firecall procedures. Besides th e capabilities for authenticator management specified in this requirement, the strength of the authentication mechanism depends on the strength of the chosen authenticator (for example, password complexity or key length in public key authentication) and the policies for validating the authenticator in the authentication process (for example, how long a password is valid or which checks are performed in public key certificate validation). For the most common authentication mechanisms, password- based and publ ic key authentication, 5.9, 5.10 and 5.11 provide further requirements. Use of component s for some operations may be restricted, requiring addition al authentication (such as tokens, keys and certificates) in order to perform some funct ions. | The requirements for the four security levels that relate to CR 1.5 are: • SL-C(IAC,component) 1: CR 1.5 • SL-C(IAC,component) 2: CR 1.5 • SL-C(IAC,component) 3: CR 1.5 (1) • SL-C(IAC,component) 4: CR 1.5 (1) | SR1.5.1 | SR 1.5 RE (1) | Hardware security for software process identity credentials | For software process and device users, the control system shall provide the capability to protect the relevant authenticators via hardware mechanisms. 5.7.3.2 Void | In addition to an identifier (see 5.6, SR 1.4 – Identifier management) an authenticator is required to prove identity. Control system authenticators include, but are not limited to, tokens, symmetric keys, private keys (part of a public/private key pair), biometrics, passwords, physical keys and key cards. Human users should take reasonable measures to safeguard authenticators, including maintaining possession of their individual authenticators, not loaning or sharing authenticators with others and reporting lost or compromi sed authenticators immediately. Authenticators have a lifecycle. When an account is created automatically a new authenticator needs to be created, in order for the account owner to be able to authenticate. For example, in a password- based system, the account has a password associated with it. Definition of the initial authenticator content could be interpreted as the administrator defining the initial password which the account management system sets for all new accounts. Being able to configure these initial values makes it harder for an attacker to guess the password between account creation and first account use (which should involve t he setting of a new password by the account owner). Some control systems are installed with unattended installers which create all necessary accounts with default passwords and some embedded devices are shipped with default passwords. Over time, these pass words often become general knowledge and are documented on the Internet. Being able to change the default passwords protects the system against unauthorized users using default passwords to gain access. Passwords can be obtained from storage or from transm ission when used in network authentication. The complexity of this can be increased by cryptographic protections such as encryption or hashing or by handshake protocols which do no t require transmission of the password at all. Still, passwords might be subject to attacks, for example brute force guessing or breaking the cryptographic protection of passwords in transit or storage. The window of opportunity can be reduced by changing/refreshing the passwords periodically. Similar considerations apply to authentication systems based on cryptographic keys. Enhanced protection can be achieved by using hardware mechanisms such as hardware security modules like trusted platform modules (TPMs). The management of authenticators should be specified in applicable secur ity policies and procedures, for example, constraints to change default authenticators, refresh periods, specification of the protection of authenticators or firecall (see 3.1.24) procedures. Lockout or loss of control due to security measures is not acceptable. If the control system is required to have a high level of availability, measures should be taken to maintain this high level of availability (such as compensating ph ysical countermeasures, duplicate keys and supervisory override). Besides the capabilities for authenticator management specified in this requirement, the strength of the authentication mechanism depends on the strength of the chosen authenticator (for example password complexity or key length in public key authentication) and the policies for validating the authenticator in the authentication process (for example how long a password is valid or which checks are performed in public key certi ficate validation). For the most common authentication mechanisms password- based and public key authentication 5.9, SR 1.7 – Strength of passw ord-based authentication, 5.10, SR 1.8 – Public key infrastructure (PKI) c ertificates and 5.11, SR 1.9 – Strength of public key authentication provide further requirements. | The requirements for the four SL levels that relate to SR 1.5 – Authenticator management are: • SL-C(IAC, control system) 1: SR 1. 5 • SL-C(IAC, control system) 2: SR 1. 5 • SL-C(IAC, control system) 3: SR 1. 5 (1) • SL-C(IAC, control system) 4: SR 1. 5 (1) | Same base identifier and enhancement sequence
10 | 1 | Base requirement | CR1.7 | CR 1.7 | CR | Strength of password- based authentication | For component s that utilize password- based authentication, those component s shall provide or integrate into a system that provides the capability to enforce c onfigurable password strength according to internationally recognized and proven password guidelines. | The ability to enforce configurable password strength, whether it is based on minimum length, variety of characters, or duration of time (the minimum being a one -time password) is necessary to assist in increasing the overall security of user chosen passwords. Generally accepted practices and recommendations can be found in documents such as [20]. | The requirements for the four security levels that relate to CR 1.7 are: • SL-C(IAC,component) 1: CR 1.7 • SL-C(IAC,component) 2: CR 1.7 • SL-C(IAC,component) 3: CR 1.7 (1) • SL-C(IAC,component) 4: CR 1.7 (1) (2) | SR1.7 | SR 1.7 | Strength of p assword -based authentication | For control systems utilizing password- based authentication, the control system shall provide the capability to enforce configurable password strength based on minimum length and variety of character types. | User authentication based on a username and a secret password is a very commonly used mechanism. Many attacks on such mechanisms focus on guessing the password (for example, dictionary attacks or targeted social engineering) or breaking the cryptographic protection of the stored password representation (for example, using rainbow tables or bruteforcing a hash collision). Increasing the size of the set of valid passwords by incr easing the number of allowed characters makes such attacks more complex, but only if the increased set size is actually used (generally users would tend to not include special characters in a password as they are perceived as harder to remember). Limiting the lifetime of a password decreases the window of opportunity for an attacker to breach a given password’s secrecy. In order to prevent users from circumventing this control by once changing their password to a new one and then immediately changing back t o their original password, a minimum lifetime for a password is commonly enforced as well. A notification to change the password prior the expiration allows the user to change the password at a convenient time according to process operations conditions. This protection can be further enhanced by limiting the reuse of passwords (preventing small sets of alternating passwords), which further decreases the usefulness of a once- breached password. Extended protection beyond password based mechanisms can be ach ieved using multifactor authentication (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication). | The requirements for the four SL levels that relate to SR 1.7 – Strength of password- based authenticati on are: • SL-C(IAC, control system) 1: SR 1. 7 • SL-C(IAC, control system) 2: SR 1. 7 • SL-C(IAC, control system) 3: SR 1. 7 (1) • SL-C(IAC, control system) 4: SR 1. 7 (1) (2) | Same base identifier and enhancement sequence
11 | 1 | Enhancement | CR1.7.1 | CR 1.7 RE (1) | CR | Password generation and lifetime restrictions for human users | © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 Component s shall provide, or integrate into a system that provides, the capability to protect against any given human user account from reusing a password for a configurable number of generations. In addition, the component shall provide the capability to enforce password minimum and maximum lifetime restrictions for human users. These capabilities shall conform to commonly accepted security industry practices. The component should provide the capability to prompt t he user t o change their password upon a configurable time prior to expiration. | The ability to enforce configurable password strength, whether it is based on minimum length, variety of characters, or duration of time (the minimum being a one -time password) is necessary to assist in increasing the overall security of user chosen passwords. Generally accepted practices and recommendations can be found in documents such as [20]. | The requirements for the four security levels that relate to CR 1.7 are: • SL-C(IAC,component) 1: CR 1.7 • SL-C(IAC,component) 2: CR 1.7 • SL-C(IAC,component) 3: CR 1.7 (1) • SL-C(IAC,component) 4: CR 1.7 (1) (2) | SR1.7.1 | SR 1.7 RE (1) | Password generation and lifetime restrictions for human users | The control system shall provide the capability to prevent any given human user account from reusing a password for a configurable number of generations. In addition, the control system shall provide the capability to enforce password minimum and maximum lifetime restrictions for human users. These capabilities shall conform with commonly accepted security industry practices. NOTE It is a commonly accepted good practice that the control system provides the capability to prompt the user to change his password upon a configurable time prior to expiration. | User authentication based on a username and a secret password is a very commonly used mechanism. Many attacks on such mechanisms focus on guessing the password (for example, dictionary attacks or targeted social engineering) or breaking the cryptographic protection of the stored password representation (for example, using rainbow tables or bruteforcing a hash collision). Increasing the size of the set of valid passwords by incr easing the number of allowed characters makes such attacks more complex, but only if the increased set size is actually used (generally users would tend to not include special characters in a password as they are perceived as harder to remember). Limiting the lifetime of a password decreases the window of opportunity for an attacker to breach a given password’s secrecy. In order to prevent users from circumventing this control by once changing their password to a new one and then immediately changing back t o their original password, a minimum lifetime for a password is commonly enforced as well. A notification to change the password prior the expiration allows the user to change the password at a convenient time according to process operations conditions. This protection can be further enhanced by limiting the reuse of passwords (preventing small sets of alternating passwords), which further decreases the usefulness of a once- breached password. Extended protection beyond password based mechanisms can be ach ieved using multifactor authentication (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication). | The requirements for the four SL levels that relate to SR 1.7 – Strength of password- based authenticati on are: • SL-C(IAC, control system) 1: SR 1. 7 • SL-C(IAC, control system) 2: SR 1. 7 • SL-C(IAC, control system) 3: SR 1. 7 (1) • SL-C(IAC, control system) 4: SR 1. 7 (1) (2) | Same base identifier and enhancement sequence
12 | 1 | Enhancement | CR1.7.2 | CR 1.7 RE (2) | CR | Password lifetime restrictions for all users (human, software process, or device) | Component s shall provide, or integrate into a system that provides, the capability to enforce password minimum and maximum lifetime restrictions for all users. | The ability to enforce configurable password strength, whether it is based on minimum length, variety of characters, or duration of time (the minimum being a one -time password) is necessary to assist in increasing the overall security of user chosen passwords. Generally accepted practices and recommendations can be found in documents such as [20]. | The requirements for the four security levels that relate to CR 1.7 are: • SL-C(IAC,component) 1: CR 1.7 • SL-C(IAC,component) 2: CR 1.7 • SL-C(IAC,component) 3: CR 1.7 (1) • SL-C(IAC,component) 4: CR 1.7 (1) (2) | SR1.7.2 | SR 1.7 RE (2) | Password lifetime restrictions for all users | The contro l system shall provide the capability to enforce password minimum and maximum lifetime restrictions for all user s. | User authentication based on a username and a secret password is a very commonly used mechanism. Many attacks on such mechanisms focus on guessing the password (for example, dictionary attacks or targeted social engineering) or breaking the cryptographic protection of the stored password representation (for example, using rainbow tables or bruteforcing a hash collision). Increasing the size of the set of valid passwords by incr easing the number of allowed characters makes such attacks more complex, but only if the increased set size is actually used (generally users would tend to not include special characters in a password as they are perceived as harder to remember). Limiting the lifetime of a password decreases the window of opportunity for an attacker to breach a given password’s secrecy. In order to prevent users from circumventing this control by once changing their password to a new one and then immediately changing back t o their original password, a minimum lifetime for a password is commonly enforced as well. A notification to change the password prior the expiration allows the user to change the password at a convenient time according to process operations conditions. This protection can be further enhanced by limiting the reuse of passwords (preventing small sets of alternating passwords), which further decreases the usefulness of a once- breached password. Extended protection beyond password based mechanisms can be ach ieved using multifactor authentication (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication). | The requirements for the four SL levels that relate to SR 1.7 – Strength of password- based authenticati on are: • SL-C(IAC, control system) 1: SR 1. 7 • SL-C(IAC, control system) 2: SR 1. 7 • SL-C(IAC, control system) 3: SR 1. 7 (1) • SL-C(IAC, control system) 4: SR 1. 7 (1) (2) | Same base identifier and enhancement sequence
13 | 1 | Base requirement | CR1.8 | CR 1.8 | CR | Public key infrastructure certificates | When public key infrastructure (PKI) is utilized, the component shall provide or integrate into a system that provides the capability to interact and operate in accordance with IEC 62443 -33 SR1.8. | The selection of an appropriate PKI should consi der the organization’s certific ate policy which should be based on the risk associated with a breach of confidentiality of the protected information. Guidance on the policy definition can be found in commonly accepted standards and guidelines, such as the Internet Engineering Task Force (IETF) Request for Comment (RFC) 3647 [22] for X.509 -based PKI. For example, the appropriate location of a certification authority (CA), whether within the control system versus on the Internet, and the list of trusted CAs should be considered in the policy and depends on the network architectur e (see also IEC 62443 -2-1 [1]). | The requirements for the four security levels that relate to CR 1.8 are: • SL-C(IAC,component) 1: Not selected • SL-C(IAC,component) 2: CR 1.8 • SL-C(IAC,component) 3: CR 1.8 • SL-C(IAC,component) 4: CR 1.8 © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | [6 empty] | No corresponding SR
14 | 1 | Base requirement | CR1.9 | CR 1.9 | CR | Strength of public key -based authentication | For component s that utilize public -key-based authentication, those component s shall provide directly or integrate into a system that provides the capability within the same IACS environment to: a) validate certificates by checking the validity of the signature of a given certificate; b) validate the certificate chain or, in the case of self -signed certificates, by deploying leaf certificates to all hosts that communicate with the subject to which the certificate is issued; c) validate certificates by checking a given certificate’s revocation status; d) establish user (human, software process or device) control of the corresponding private key; e) map the authenticated identity to a user (human, software process or devi ce); and f) ensure that the algorithms and keys used for the public key authentication conform to 8.5. | To meet the requirements in 5.11.1 does not necessarily require a real time connection to a certificate authority. Alternative out -of-band methods may be used to meet the requirements in 5.11.1. For example, a disconnected system could install and update certifications using manual out -of-band processes. Public/private key cryptogra phy strongly depends on the secrecy of a given subject’s private key and proper handling of the trust relationships. When verifying a trust between two entities based on public key authentication, it is essential to trace the public key certificate to a trusted entity. A common implementation error in certificate validation is to only check the validity of a certificate’s signature, but not checking the trust in the signer. In a PKI setting, a signer is trusted if they are a trusted CA or have a certificate issued by a trusted CA, thus all verifiers need to trace certificates presented to them back to a trusted CA. If such a chain of trusted CAs cannot be established, the presented certificate should not be trusted. If self -signed certificates are used instead of a PKI, the certificate subject itself signed its certificate, thus there never is a trusted third- party or CA. This should be compensated by deploying the self -signed public key certificates to all peers that need to validate them via an otherwise secured mechanism (for example, configuration of all peers in a trusted environment). Trusted certificates need to be distributed to peers through secure channels. During the validation process, a self -signed certificate should only be trusted if it is alre ady present in the list of trusted certificates of the validating peer. The set of trusted certificates should be configured to the minimum necessary set. In both cases, validation needs to also consider the possibility that a certificate is revoked. In a PKI setting this is typically done by maintaining certificate revocation lists (CRLs) or running an online certificate status protocol (OCSP) server. When revocation checking is not available due to control system constraints, mechanisms such as a short certificate lifetime can compensate for the lack of timely revocation information. Note that short lifetime certificates can sometimes create significant operational issues in a control system environment. It is expected that most component s will integrate into an IACS and leverage the key authentication mechanisms provided by the underlying IACS. When implementing public key authentication at the component -level of an IACS, protection of the key becomes a primary concern and objective of key storage on that component. Care should be taken in the implementation to ensure that any private keys stored within the component cannot be retrieved or tampered with (see 5.7). NOTE Tamper resistant design methodologies and technologies are available to assist with designing a secure private key protection mechanism. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | The requirements for the four security levels that relate to CR 1.9 are: • SL-C(IAC,component) 1: Not selected • SL-C(IAC,component) 2: CR 1.9 • SL-C(IAC,component) 3: CR 1.9 (1) • SL-C(IAC,component) 4: CR 1.9 (1) | SR1.9 | SR 1.9 | Strength of public key authentication | For control systems utilizing public key authentication, the control system shall provide the capability to: a) validate certificates by checking the validity of the signature of a given certificate; b) validate certificates by constructing a certification path to an accepted CA or in the case of self-signed certificates by deploying l eaf certificates to all hosts which communicate with the subject to which the certificate is issued; c) validate certificates by checking a given certificate’s revocation status; d) establish user (human, software process or device) control of the corresponding private key; and e) map the authenticated identity to a user (human, software process or device). | Public/private key cryptography strongly depends on the secrecy of a given subject’s private key and proper handling of the trust relationships. When verifying a trust between two entities based on public key authentication, it is essential to trace the public key certificate to a trusted entity. A common implementation error in certificate validation is to only check the validi ty of a certificate’s signature, but not checking the trust in the signer. In a PKI setting, a signer is trusted if they are a trusted CA or have a certificate issued by a trusted CA, thus all verifiers need to trace certificates presented to them back to a trusted CA. If such a chain of trusted CAs canno t be established, the presented certificate should not be trusted. If self -signed certificates are used instead of a PKI, the certificate subject itself signed its certificate, thus there never is a trusted third -party or CA. This should be compensated by deploying the self -signed public key certificates to all peers that need to validate them via an otherwise secured mechanism (for example, configuration of all peers in a trusted environment). Trusted certificates need to be distributed to peers through secure channels. During the validation process, a self -signed certificate should only be trusted if it is already present in the list of trusted certificates of the validating peer. The set of trusted certifi cates should be configured to the minimum necessary set. In both cases, validation needs to also consider the possibility that a certificate is revoked. In a PKI setting this is typically done by maintaining certificate revocation lists (CRLs) or running an online certificate status protocol (OCSP) server. When revocation checking is not available due to control system constraints, mechanisms such as a short certificate lifetime can compensate for the lack of timely revocation information. Note that short lifetime certificates can sometimes create significant operational issues in a control system environment. | The requirements for the four SL levels that relate to SR 1.9 – Strength of public key authentication are: • SL-C(IAC, control system) 1: Not Selected • SL-C(IAC, control system) 2: SR 1. 9 • SL-C(IAC, control system) 3: SR 1. 9 (1) • SL-C(IAC, control system) 4: SR 1. 9 (1) | Same base identifier and enhancement sequence
15 | 1 | Enhancement | CR1.9.1 | CR 1.9 RE (1) | CR | Hardware security for public key -based authentication | Component s shall provide the capability to protect critical, long -lived private keys via hardware mechanisms. | To meet the requirements in 5.11.1 does not necessarily require a real time connection to a certificate authority. Alternative out -of-band methods may be used to meet the requirements in 5.11.1. For example, a disconnected system could install and update certifications using manual out -of-band processes. Public/private key cryptogra phy strongly depends on the secrecy of a given subject’s private key and proper handling of the trust relationships. When verifying a trust between two entities based on public key authentication, it is essential to trace the public key certificate to a trusted entity. A common implementation error in certificate validation is to only check the validity of a certificate’s signature, but not checking the trust in the signer. In a PKI setting, a signer is trusted if they are a trusted CA or have a certificate issued by a trusted CA, thus all verifiers need to trace certificates presented to them back to a trusted CA. If such a chain of trusted CAs cannot be established, the presented certificate should not be trusted. If self -signed certificates are used instead of a PKI, the certificate subject itself signed its certificate, thus there never is a trusted third- party or CA. This should be compensated by deploying the self -signed public key certificates to all peers that need to validate them via an otherwise secured mechanism (for example, configuration of all peers in a trusted environment). Trusted certificates need to be distributed to peers through secure channels. During the validation process, a self -signed certificate should only be trusted if it is alre ady present in the list of trusted certificates of the validating peer. The set of trusted certificates should be configured to the minimum necessary set. In both cases, validation needs to also consider the possibility that a certificate is revoked. In a PKI setting this is typically done by maintaining certificate revocation lists (CRLs) or running an online certificate status protocol (OCSP) server. When revocation checking is not available due to control system constraints, mechanisms such as a short certificate lifetime can compensate for the lack of timely revocation information. Note that short lifetime certificates can sometimes create significant operational issues in a control system environment. It is expected that most component s will integrate into an IACS and leverage the key authentication mechanisms provided by the underlying IACS. When implementing public key authentication at the component -level of an IACS, protection of the key becomes a primary concern and objective of key storage on that component. Care should be taken in the implementation to ensure that any private keys stored within the component cannot be retrieved or tampered with (see 5.7). NOTE Tamper resistant design methodologies and technologies are available to assist with designing a secure private key protection mechanism. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | The requirements for the four security levels that relate to CR 1.9 are: • SL-C(IAC,component) 1: Not selected • SL-C(IAC,component) 2: CR 1.9 • SL-C(IAC,component) 3: CR 1.9 (1) • SL-C(IAC,component) 4: CR 1.9 (1) | SR1.9.1 | SR 1.9 RE (1) | Hardware security for public key authentication | The control system shall provide the capability to protect the relevant private keys via hardware mechanisms according to commonly accepted security industry practices and recommendations. 5.11.3.2 Void | Public/private key cryptography strongly depends on the secrecy of a given subject’s private key and proper handling of the trust relationships. When verifying a trust between two entities based on public key authentication, it is essential to trace the public key certificate to a trusted entity. A common implementation error in certificate validation is to only check the validi ty of a certificate’s signature, but not checking the trust in the signer. In a PKI setting, a signer is trusted if they are a trusted CA or have a certificate issued by a trusted CA, thus all verifiers need to trace certificates presented to them back to a trusted CA. If such a chain of trusted CAs canno t be established, the presented certificate should not be trusted. If self -signed certificates are used instead of a PKI, the certificate subject itself signed its certificate, thus there never is a trusted third -party or CA. This should be compensated by deploying the self -signed public key certificates to all peers that need to validate them via an otherwise secured mechanism (for example, configuration of all peers in a trusted environment). Trusted certificates need to be distributed to peers through secure channels. During the validation process, a self -signed certificate should only be trusted if it is already present in the list of trusted certificates of the validating peer. The set of trusted certifi cates should be configured to the minimum necessary set. In both cases, validation needs to also consider the possibility that a certificate is revoked. In a PKI setting this is typically done by maintaining certificate revocation lists (CRLs) or running an online certificate status protocol (OCSP) server. When revocation checking is not available due to control system constraints, mechanisms such as a short certificate lifetime can compensate for the lack of timely revocation information. Note that short lifetime certificates can sometimes create significant operational issues in a control system environment. | The requirements for the four SL levels that relate to SR 1.9 – Strength of public key authentication are: • SL-C(IAC, control system) 1: Not Selected • SL-C(IAC, control system) 2: SR 1. 9 • SL-C(IAC, control system) 3: SR 1. 9 (1) • SL-C(IAC, control system) 4: SR 1. 9 (1) | Same base identifier and enhancement sequence
16 | 1 | Base requirement | CR1.10 | CR 1.10 | CR | Authenticator feedback | When a component prov ides an authentication capability, the component shall provide the capability to obscure feedback of authenticator information during the authentication process. | Obscuring feedback protects the information from possible exploitation by unauthorized individuals, for example, displaying asterisks or other random characters when a human user types in a username and/or password obscures feedback of authentication information. Other examples include the entry of secure socket shell (SSH) token and one- time passwords. The authenticating entity should not provide any hint as to the reason for the authentication failure, such as “unknown user name.” | The requirements for the four SL levels that relate to C R 1.1 0 are: • SL-C(IAC,component) 1: CR 1.10 • SL-C(IAC,component) 2: CR 1.10 • SL-C(IAC,component) 3: CR 1.10 • SL-C(IAC,comp onent) 4: CR 1.10 | SR1.10 | SR 1.10 | Authenticator feedback | The control system shall provide the capability to obscure feedback of authentication information during the authentication process. | Obscuring feedback protects the information from possible exploitatio n by unauthorized individuals, f or example, displaying asterisks or other random characters when a human user types in a password obscures feedback of authentication information. Other examples include the entry of wired equivalent priv acy (WEP) keys, secure socket shell (SSH) token entry and RSA one -time passwords. The authenticating entity should not provide any hint as to the reason for the authentication failure, such as “unknown user name”. | The requirements for the four SL levels that relate to SR 1.10 – Authenticator feedback are: • SL-C(IAC, control system) 1: SR 1. 10 • SL-C(IAC, control system) 2: SR 1.10 • SL-C(IAC, control system) 3: SR 1. 10 • SL-C(IAC, control system) 4: SR 1. 10 | Same base identifier and enhancement sequence
17 | 1 | Base requirement | CR1.11 | CR 1.11 | CR | Unsuccessful login attempts | When a component provides an authentication capability, the component shall provide the capability to: a) enforce a limit of a configurable number of consecutive invalid access attempts by any user (human, software process or device) during a configurable time period; and b) deny access for a specified period of time or until unlocked by an administrator when this limit has been reached. An administrator may unlock an account prior to the expiration of the timeout period. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | Due to the potential for denial of service, the number of consecutive invalid access attempts may be limited. If enabled, the application or device may automatically reset to zero the number of access attempts after a predetermined time period established by the applicable security policies and procedures. Resetting the access attempts to zero will allow users (human, software process or device) to gain access if they have the corr ect login credentials. Automatic (without human intervention) denial of access for control system operator workstations or nodes should not be used when immediate operator responses are required in emergency situations. All lockout mechanisms should consider functional requirements for continuous operations so as to mitigate adverse denial of service operating conditions which could result in system failures or compromising the safety of the system. Allowing interactive logins to an account used for critica l services could provide a potential for denial of service or other abuse. | The requirements for the four SL levels that relate to C R 1.1 1 are: • SL-C(IAC,component) 1: CR 1.11 • SL-C(IAC,component) 2: CR 1.11 • SL-C(IAC,component) 3: CR 1.11 • SL-C(IAC,component) 4: CR 1.11 | SR1.11 | SR 1.11 | Unsuccessful login attempts | The control system shall provide the capability to enforce a limit of a configurable number of consecutive invalid access attempts by an y user (human, software process or device) during a configurable time period. The control system shall provide the capability to deny access for a specified period of time or until unlocked by an administrator when this limit has been exceede d. For system accounts on behalf of which critical services or servers are run, the control system shall provide the capability to disallow interactive logons. | Due to the potential for denial of service, the number of consecutive invalid access attempts may be limited. If enabled, the control system may automatically reset to zero the number of access attempts after a predetermined time period established by the applicable security polic ies and procedures. Resetting the access attempts to zero will allow users (human, software process or device) to gain access if they have the correct login identifier. Automatic denial of access for control system operator workstations or nodes should not be used when immediate operator responses are required in emergency situations. All lockout mechanisms should consider functional requirements for continuous operations so as to mitigate adverse denial of service operating conditions which could result in total system f ailure or injury to personnel. Allowing interactive logins to an account used for critical services could provide a potential for denial of service or other abuse. | The requirements for the four SL levels that relate to SR 1.11 – Unsuccessful login attempts are: • SL-C(IAC, control system) 1: SR 1. 11 • SL-C(IAC, control system) 2: SR 1. 11 • SL-C(IAC, control system) 3: SR 1. 11 • SL-C(IAC, control system) 4: SR 1. 11 | Same base identifier and enhancement sequence
18 | 1 | Base requirement | CR1.12 | CR 1.12 | CR | System use notification | When a component provides local human user access/HMI, it shall provide the capability to display a system use notification message before authenticating. The system use notification message shall be configurable by authorized personnel. | Privacy and security policies and pr ocedures need to be consistent with applicable laws, directives, policies, regulations, standards and guidance. Often, the main justification for this requirement is legal prosecution of violators and proving intentional breach. This capability is thus nec essary to support policy requirements, and might improve IACS security because it can be used as a deterrent. System use notification messages can be implemented in the form of warning banners displayed when individuals log in to the control system. A warn ing banner implemented as a posted physical notice in the control system facility does not protect against remote login issues. Examples of elements for inclusion in the system use notification message are: a) that the individual is accessing a system owned by the asset owner; b) that system usage may be monitored, recorded and subject to audit; c) that unauthorized use of the system is prohibited and subject to crimi nal and/or civil penalties; and d) that use of the system indicates consent to monitoring and recording. | The requirements for the four SL levels that relate to C R 1.1 2 are: • SL-C(IAC,component) 1: CR 1.12 • SL-C(IAC,component) 2: CR 1.12 • SL-C(IAC,component) 3: CR 1.12 • SL-C(IAC,component) 4: CR 1.12 | SR1.12 | SR 1.12 | System use notification | The control system shall provide the capability to display a system use notification message before authenticating. The system use notification message shall be configurable by authorized per sonnel. | Privacy and security policies and procedures need to be consistent with applicable laws, directives, policies, regulat ions, standards and guidance. Often the main justification for this requirement is legal prosecution of violators and proving intentional breach. This capability is thus necessary to support policy requirements, and does not improve IACS security. System use notification messages can be implemented in the form of warning banners displayed when individuals log in to the control system. A warning banner implemented as a posted physical notice in the control system facility does not protect against remote login issues. Examples of elements for inclusion in the system use notification message are: a) that the individual is accessing a specific control system; b) that system usage may be monitored, recorded and subject to audit; c) that unauthorized use of the system is prohibited and subject to criminal and/or civil penalties; and d) that use of the system indicates consent to monitoring and recording. | The requirements for the four SL levels that relate to SR 1.12 – System use notification are: • SL-C(IAC, control system) 1: SR 1. 12 • SL-C(IAC, control system) 2: SR 1. 12 • SL-C(IAC, control system) 3: SR 1. 12 • SL-C(IAC, control system) 4: SR 1. 12 5.15 SR 1.1 3 – Access via untrusted networks Requirement 5.15.1The control system shall provide the capability to monitor and control all methods of access to the control system via untrusted networks. Rationale and supplemental guidance 5.15.2 Examples of access to the control system via untrusted networks typically include remote access methods (such as dial-up, broadband and wireless) as well as connections from a company’s office (non -control system) network. The control system should restrict access achieved through dial -up connections (for example, limiting dial -up access based upon the source of the request) or protect against unauthorized connections or subversion of authorized connections (for example, using virtua l private network technology). Access via untrusted networks to geographically remote control system component locations (for example, control centres and field locations) should only be enabled when necessary and authenticated. Security policies and procedures may require multifactor authentication for remote user access to the control system. Requirement enhancements 5.15.3 5.15.3.1 SR 1.13 RE 1 – Explicit access request approval The control system shall provide the capability to deny access requests via untrusted networks unless approved by an assigned role. 5.15.3.2 Void Security levels 5.15.4 The requirements for the four SL levels that relate to SR 1.13 – Access via untrusted networks are: • SL-C(IAC, control system) 1: SR 1.1 3 • SL-C(IAC, control system) 2: SR 1.1 3 (1) • SL-C(IAC, control system) 3: SR 1.1 3 (1) • SL-C(IAC, control system) 4: SR 1.1 3 (1) 6 FR 2 – Use control 6.1 Purpose and SL-C(UC) descriptions Enforce the assigned privileges of an authenticated user (human, software process or device) to perform the requested action on the IACS and monitor the use of these privileges. • SL 1 – Restrict use of the IACS according to specified privileges to protect against casual or coincidental misuse. • SL 2 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 6.2 Rationale Once the user is identified and authenticated, the control system has to restrict the allowed actions to the authorized use of the control system. Asset owners and system integrators will have to assign, to each user (human, software process or device), group, ro le, etc. (see 5.6, SR 1.4 – Identifier management) the privileges defining the authorized use of the IACS. The goal of use control is to protect against unauthorized actions on the control system resources by verifying that the necessary privileges have been granted before a llowing a user to perform the actions. Examples of actions are reading or writing data, downloading program s and setting configurations. Recommendations and guidelines should include mechanisms that will operate in mixed modes. For example, some control system resources require strong use control protection, such as restrictive privileges, and others do not. By extension, use control requirements need to be extended to data at rest. User privileges may vary based on time- ofday/date, location and means by which access is made. | Same base identifier and enhancement sequence
19 | 1 | Base requirement | CR1.14 | CR 1.14 | CR | Strength of symmetric key -based authentication | For components that utilize symmetric key s, the component shall provide the capability to: a) establish the mutual trust using the symmetric key; b) store securely the shared secret (the authentication is valid as long as the shared secret remains secret); c) restrict access to the shared secret; and d) ensure that the algorithms and keys used for the symmetric key authentication conform to 8.5. | and supplemental gui dance Means should be defined for installing the keys into the component. This may include installing and managing the component key using out -of-band methods. This is necessary since a compromise of any symmetric keys that are stored within the component could lead to a full compromise of the system using those keys. In practice, there are two basic ways to perform the secure authentication of a device to another: either using asymmetric cryptography (see 5.11) or by using symmetric cryptography. The choice between asymmetric and symmetric is dictated by several criteria, like key management, trust provisioning, legacy support and efficiency. Examples of symmetric k ey authentication schemes are Needham -Schröder or Kerberos. When symmetric key authentication is used, the party uses a secret key they have learned in the past (for example, through trust provisioning). The party proves their claimed identity by proving knowledge of the secret key (for example, by answering a challenge submitted by the other party, the examiner). The examiner has the knowledge of the same secret (also learned in the past through trust provisioning) and is able to compute the answer to the challenge performing the same cryptographic operations as the prover. The examiner can then compare the answer of the prover with its own computation. If they match, the exam iner is convinced that the prover is the one they claim to be and the process can be conducted the other way around, switching roles, to achieve mutual -authentication. This mechanism is secure only if the shared secret is only known by the prover and the examiner and if the secret is diversified per prover. One instance of such a mechanism is the proper use of cipher -based message authentication code (CMAC) computations or alternatively the Galois counter mode (GCM)/Galois message authentication code (GMAC) operation modes. | The requirements for the four SL levels that relate to CR 1.14 are: • SL-C(IAC,control system) 1: Not selected • SL-C(IAC,control system) 2: CR 1.14 • SL-C(IAC,control system) 3: CR 1.14 (1) • SL-C(IAC,control system) 4: CR 1.14 (1) 6 FR 2 – Use control 6.1 Purpose and SL-C(UC) descriptions Enforce the assigned privileges of an authenticated user (human, software process or device) to perform the requested action on the component and monitor the use of these privileges. • SL 1 – Restrict use of the IACS according to specified privi leges to protect against casual or coincidental misuse. • SL 2 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Restrict use of the IACS according to specified privileg es to protect against circumvention by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 6.2 Rationale Once the user is identified and authenticated, the component should restrict the allowed actions to the authorized use of the component. Asset owners and system integrators will have to assign, to each user (human, software process or device), group, role, etc. (see 4.5), the privileges defining the authorized use of the component. The goal of use control is to protect against unauthorized actions on the component ’s resources by verifying that the necessary privileges have been grant ed before allowing a user to perform the actions. Examples of actions are reading or writing data, downloading programs and setting configurations. Recommendations and guidelines should include mechanisms that will operate in mixed modes. For example, some component resources require strong use control protection, such as restrictive privileges, and others do not. By extension, use control requirements should be extended to data at rest. User privileges may vary based on time- ofday/date, location and means by which access is made. | [6 empty] | No corresponding SR
20 | 1 | Enhancement | CR1.14.1 | CR 1.14 RE (1) | CR | Hardware security for symmetric key -based authentication | Components shall provide the capability to protect critical, long lived symmetric keys via hardware mechanisms. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | and supplemental gui dance Means should be defined for installing the keys into the component. This may include installing and managing the component key using out -of-band methods. This is necessary since a compromise of any symmetric keys that are stored within the component could lead to a full compromise of the system using those keys. In practice, there are two basic ways to perform the secure authentication of a device to another: either using asymmetric cryptography (see 5.11) or by using symmetric cryptography. The choice between asymmetric and symmetric is dictated by several criteria, like key management, trust provisioning, legacy support and efficiency. Examples of symmetric k ey authentication schemes are Needham -Schröder or Kerberos. When symmetric key authentication is used, the party uses a secret key they have learned in the past (for example, through trust provisioning). The party proves their claimed identity by proving knowledge of the secret key (for example, by answering a challenge submitted by the other party, the examiner). The examiner has the knowledge of the same secret (also learned in the past through trust provisioning) and is able to compute the answer to the challenge performing the same cryptographic operations as the prover. The examiner can then compare the answer of the prover with its own computation. If they match, the exam iner is convinced that the prover is the one they claim to be and the process can be conducted the other way around, switching roles, to achieve mutual -authentication. This mechanism is secure only if the shared secret is only known by the prover and the examiner and if the secret is diversified per prover. One instance of such a mechanism is the proper use of cipher -based message authentication code (CMAC) computations or alternatively the Galois counter mode (GCM)/Galois message authentication code (GMAC) operation modes. | The requirements for the four SL levels that relate to CR 1.14 are: • SL-C(IAC,control system) 1: Not selected • SL-C(IAC,control system) 2: CR 1.14 • SL-C(IAC,control system) 3: CR 1.14 (1) • SL-C(IAC,control system) 4: CR 1.14 (1) 6 FR 2 – Use control 6.1 Purpose and SL-C(UC) descriptions Enforce the assigned privileges of an authenticated user (human, software process or device) to perform the requested action on the component and monitor the use of these privileges. • SL 1 – Restrict use of the IACS according to specified privi leges to protect against casual or coincidental misuse. • SL 2 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Restrict use of the IACS according to specified privileg es to protect against circumvention by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 6.2 Rationale Once the user is identified and authenticated, the component should restrict the allowed actions to the authorized use of the component. Asset owners and system integrators will have to assign, to each user (human, software process or device), group, role, etc. (see 4.5), the privileges defining the authorized use of the component. The goal of use control is to protect against unauthorized actions on the component ’s resources by verifying that the necessary privileges have been grant ed before allowing a user to perform the actions. Examples of actions are reading or writing data, downloading programs and setting configurations. Recommendations and guidelines should include mechanisms that will operate in mixed modes. For example, some component resources require strong use control protection, such as restrictive privileges, and others do not. By extension, use control requirements should be extended to data at rest. User privileges may vary based on time- ofday/date, location and means by which access is made. | [6 empty] | No corresponding SR
21 | 2 | Base requirement | CR2.1 | CR 2.1 | CR | Authorization enforcement | Component s shall provide an authorization enforcement mechanism for all identified and authenticated users based on their assigned responsibilities. | and supplemental guidanc e Use control policies (for example, identity -based policies, role- based policies and rule -based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to c ontrol usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software processes, programs and domains). © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 After the control system has verified the identity of a user (human, software process or devic e) (see 5.3 and 5.4), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role -based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mechanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qualified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four security levels that relate to CR 2.1 are: • SL-C(UC,component) 1: CR 2.1 • SL-C(UC,component) 2: CR 2.1 (1) (2) • SL-C(UC,co mponent) 3: CR 2.1 (1) (2) (3) • SL-C(UC,component) 4: CR 2.1 (1) (2) (3) (4) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR2.1 | SR 2.1 | Authorization enforcement | On all interfaces, t he control system shall provide the capability to enforce authorizations assigned to all human users for controlling use of the control system to support segregation of duties and least privilege. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4) | Same base identifier and enhancement sequence
22 | 2 | Enhancement | CR2.1.1 | CR 2.1 RE (1) | CR | Authorization enforcement for all users (humans, software processes and devices) | Componen ts shall provide an authorization enforcement mechanism for all users based on their assigned responsibilities and least privilege. | and supplemental guidanc e Use control policies (for example, identity -based policies, role- based policies and rule -based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to c ontrol usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software processes, programs and domains). © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 After the control system has verified the identity of a user (human, software process or devic e) (see 5.3 and 5.4), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role -based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mechanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qualified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four security levels that relate to CR 2.1 are: • SL-C(UC,component) 1: CR 2.1 • SL-C(UC,component) 2: CR 2.1 (1) (2) • SL-C(UC,co mponent) 3: CR 2.1 (1) (2) (3) • SL-C(UC,component) 4: CR 2.1 (1) (2) (3) (4) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR2.1.1 | SR 2.1 RE (1) | Authorization enforcement for all users | On all interfaces, the control system shall provide the capability to enforce authorizations assigned to all users (humans, software processes and devices) for controlling use of the control system to support segregation of duties and least privilege. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4) | Same base identifier and enhancement sequence
23 | 2 | Enhancement | CR2.1.2 | CR 2.1 RE (2) | CR | Permission mapping to roles | Component s shall, directly or through a compensating security mechanism, provide for an authorized role to define and modify the mapping of permissions to roles for all human users. Roles should not be limited to fixed nested hierarchies in which a higher -level role is a super set of a lesser privileged role. For example, a system administrator should not necessarily encompass operator privileges. NOTE 1 This RE is applicable to software processes and devices as well. | and supplemental guidanc e Use control policies (for example, identity -based policies, role- based policies and rule -based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to c ontrol usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software processes, programs and domains). © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 After the control system has verified the identity of a user (human, software process or devic e) (see 5.3 and 5.4), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role -based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mechanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qualified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four security levels that relate to CR 2.1 are: • SL-C(UC,component) 1: CR 2.1 • SL-C(UC,component) 2: CR 2.1 (1) (2) • SL-C(UC,co mponent) 3: CR 2.1 (1) (2) (3) • SL-C(UC,component) 4: CR 2.1 (1) (2) (3) (4) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR2.1.2 | SR 2.1 RE (2) | Permissi on mapping to roles | The control system shall provide the capability for an authorized user or role to define and modify the mapping of permissions to roles for all human users. NOTE 1 It is a commonly accepted good practice to not limit roles to fixed nested hierarchies in which a higher level role is a superset of a lesser privileged role. For example, a system administrator generally does not necessarily encompass operator privileges. NOTE 2 This RE is applicable to software processes and devices as w ell. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4) | Same base identifier and enhancement sequence
24 | 2 | Enhancement | CR2.1.3 | CR 2.1 RE (3) | CR | Supervisor override | Component s shall support a supervisor manual override for a configurable time or sequence of events. NOTE 2 Implementation of a controlled, audited and manual override of automated mechanisms in the event of emergencies or other serious events allows a supervisor to enable an operator to quickly react to unusual conditions without closing the current session and establishing a new session as a higher privilege human user. | and supplemental guidanc e Use control policies (for example, identity -based policies, role- based policies and rule -based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to c ontrol usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software processes, programs and domains). © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 After the control system has verified the identity of a user (human, software process or devic e) (see 5.3 and 5.4), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role -based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mechanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qualified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four security levels that relate to CR 2.1 are: • SL-C(UC,component) 1: CR 2.1 • SL-C(UC,component) 2: CR 2.1 (1) (2) • SL-C(UC,co mponent) 3: CR 2.1 (1) (2) (3) • SL-C(UC,component) 4: CR 2.1 (1) (2) (3) (4) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR2.1.3 | SR 2.1 RE (3) | Supervisor override | The control system shall support supervisor manual override of the current human user authorizations for a configurable time or event sequence. NOTE Implementation of a controlled, audited and manual override of automated mechanisms in the event of emergencies or other serious events is often needed. This allows a supervisor to enable an operator to quickly react to unusual conditions without closing the current session and establishing a new session as a higher privil ege human user. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4) | Same base identifier and enhancement sequence
25 | 2 | Enhancement | CR2.1.4 | CR 2.1 RE (4) | CR | Dual approval | Component s shall support dual approval when action can result in serious impact on the industrial process. Dual approval should be limited to actions which require a very high level of confidence that they will be performed reliably and correctly. Requiring dual approval provides emphasis to the seriousness of consequences that would result from failure of a correct action. An example of a situation in which dual approval is required would be a change to a set point of a critical industrial process. Dual approval mechanisms should not be employed when an immediate response is necessar y to safeguard HSE consequences, for example, emergency shutdown of an industrial process. | and supplemental guidanc e Use control policies (for example, identity -based policies, role- based policies and rule -based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to c ontrol usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software processes, programs and domains). © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 After the control system has verified the identity of a user (human, software process or devic e) (see 5.3 and 5.4), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role -based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mechanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qualified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four security levels that relate to CR 2.1 are: • SL-C(UC,component) 1: CR 2.1 • SL-C(UC,component) 2: CR 2.1 (1) (2) • SL-C(UC,co mponent) 3: CR 2.1 (1) (2) (3) • SL-C(UC,component) 4: CR 2.1 (1) (2) (3) (4) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR2.1.4 | SR 2.1 RE (4) | Dual approval | The control system shall support dual approval where an action can result in serious impact on the industrial process. NOTE It is a commonly accepted good practice to limit dual approval to actions which require a very high level of confidence that they will be performed reliably and correctly. Requiring dual approval provides emphasis to the seriousness of consequences that would result from failure of a correct action. An example of a situation in which dual approval is required would be a change to a set point of a critical industrial process. It is a commonly accepted good practice to not employ dual approval mechanisms when an immediate response is necessary to safeguard HSE consequences, for example, emergency shutdown of an industrial process. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4) | Same base identifier and enhancement sequence
26 | 2 | Base requirement | CR2.2 | CR 2.2 | CR | Wireless use control | If a component supports usage through wireless interfaces it shall provide the capability to integrate into the system that supports usage authorization, monitoring and restrictions according to commonly accepted industry practices. | Wireless use control may be implemented in different devices that make up the s ystem. Network devices may be one of the devices that assist with use control through controls such as network admission control. For devices and applications that utilize wireless networks those devices should be able to properly utilize wireless network protection such as network admission control. Component s may also implement different limitations on access based on whether the access is from wireless devices or wired devices. This does place a need that the component be able to distinguish whether the interface is through wireless or not. Some network devices provide the capability to scan for unauthorized wireless network activity in the wireless spectrum. In order to prevent a negative impact on the performance of the control system functionality, it is a good practice to deploy dedicated devices to perform checks for unauthorized network activity. | The requirements for the four SL levels that relate to CR 2.2 are: • SL-C(UC, component) 1: CR 2.2 • SL-C(UC, component) 2: C R 2.2 • SL-C(UC, component) 3: C R 2.2 • SL-C(UC, component) 4: C R 2.2 | SR2.2 | SR 2.2 | W ireless use control | The control system shall provide the capability to authorize, monitor and enforce usage restrictions for wireless connectivity to the control system according to commonly accepted security industry practices. | Any wireless technology can, and in most cases should, be considered just another communication protocol option, and thus subject to the same IACS security requirements as any other communication type utilized by the IACS. However, a risk analysis may result in a requirement for wireless IACS components to support higher use control capabilities than are typically required of wired systems for the same use case and SL-T. Regulatory differences may also result in different required capa bilities between wired and wireless communications. As noted in 5.8, SR 1.6 – Wireless access management, wireless technologies include, but are not limited to, microwave, satellite, packet radio, IEEE 802.11x, IEEE 802.15.4 (ZigBee, IEC 62591 – Wireless HART®, ISA -100.11a), IEEE 802.15.1 (Bluetooth), wireless LAN mobile routers, mobile phones with tethering and various infrared technologies. | The requirements for the four SL levels that relate to SR 2.2 – Wireless use control are: • SL-C(UC, control system) 1: SR 2.2 • SL-C(UC, control system) 2: SR 2. 2 • SL-C(UC, control system) 3: SR 2. 2 (1) • SL-C(UC, control system) 4: SR 2. 2 (1) | Same base identifier and enhancement sequence
27 | 2 | Base requirement | CR2.5 | CR 2.5 | CR | Session lock | If a component provides a human user interface, whether accessed locally or via a network, the component shall provide the capability a) to protect against further access by initiating a session lock after a configurable time period of inactivity or by manual initiation by the user (human, software process or device); and b) for the session lock to remain in effect until the human user who owns the session, or another authorized human user, re-establishes access using appropriate identification and authentication procedures. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | Session locks are used to prevent access to specified workstations or nodes. Component s should activate session lock mechanisms automatically after a configurable time period. In most cases, the session locks are configured at the system level. Session lo cks implemented as part of this requirement may be pre- empted or limited by remote session termination, as defined in 6.8. | The requirements for the four SL levels that relate to CR 2.5 are: • SL-C(UC, component) 1: CR 2.5 • SL-C(UC, component) 2: CR 2.5 • SL-C(UC, component) 3: CR 2.5 • SL-C(UC, component) 4: CR 2.5 | SR2.5 | SR 2.5 | Session lock | The control system shall provide the capability to prevent further access by initiating a session lock after a configurable time period of inactivity or by manual initiation. The session lock shall remain in effect until the human user who owns the session or another author ized human user re-establishes access using appropriate identification and authentication procedures. | The entity responsible for a control system should employ session lock to prevent access to specified workstations or nodes. The control system should activate session lock mechanisms automatically after a configurable time period for designated workstations or nodes. In some cases, session lock for control system operator workstations or nodes is not advised (for example, sessions which are required for immediate operator responses in emergency situations). Session locks are not a substitute for logging out of the control system. In situations where the control system cannot support session lock, the responsible entity sh ould employ appropriate compensating countermeasures (for example, providing increased physical security, personnel security and auditing measures). | The requirements for the four SL levels that relate to SR 2.5 – Session lock are: • SL-C(UC, control system) 1: SR 2.5 • SL-C(UC, control system) 2: SR 2.5 • SL-C(UC, control system) 3: SR 2.5 • SL-C(UC, control system) 4: SR 2.5 | Same base identifier and enhancement sequence
28 | 2 | Base requirement | CR2.6 | CR 2.6 | CR | Remote session termination | If a component supports remote sessions, the component shall provide the capability to terminate a remote session either automatically after a configurable time period of inactivity, manually by a local authority, or manually by the user (human, software process or device) who initiated the session. | A remote session is initiated whenever a component is accessed across the boundary of a zone defined by the asset owner based on their risk assessment. This requirement may be limited to s essions that are used for component monitoring and maintenance activities (not critical operations) based on the risk assessment of the control system and security policies and procedures. Some components may not allow sessions to be terminated as the session might be part of an essential function of the component. | The requirements for the four SL levels that relate to CR 2.6 are: • SL-C(UC, component) 1: Not selected • SL-C(UC, component) 2: CR 2.6 • SL-C(UC, component) 3: CR 2.6 • SL-C(UC, component) 4: CR 2.6 | SR2.6 | SR 2.6 | Remote session termination | The control system shall provide the capability to terminate a remote session either automatically after a configurable time period of inactivity or manually by the user who initiated the session. | A remote session is initiated whenever a control system is accessed across the boundary of a zone defined by the asset owner based on their risk assessment. This requirement may be limited to sessions that are used for control system monitoring and maintenance activities (not critical operations) based on the r isk assessment of the control system and security polic ies and procedures. Some control systems or components may not allow sessions to be terminated. | The requirements for the four SL levels that relate to SR 2.6 – Remote session termination are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: SR 2. 6 • SL-C(UC, control system) 3: SR 2. 6 • SL-C(UC, control system) 4: SR 2. 6 | Same base identifier and enhancement sequence
29 | 2 | Base requirement | CR2.7 | CR 2.7 | CR | Concurrent session control | Component s shall provide the capability to limit the number of concurrent sessions per interface for any given user (human, software process or device). © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | A resource starvation DoS might occur if a limit is not imposed. There is a trade- off between potentially locking out a specific user versus locking out all users and services due to a lack of resources. Product supplier and/or system integrator guidance is likely required to provide sufficient information as to how the number of concur rent sessions value should be assigned. | The requirements for the four SL leve ls that relate to CR 2.7 are: • SL-C(UC, component) 1: Not selected • SL-C(UC, component) 2: Not selected • SL-C(UC, component) 3: CR 2.7 • SL-C(UC, component) 4: CR 2.7 | SR2.7 | SR 2.7 | Concurrent session control | The control system shall provide the capability to limit the number of concurrent sessions per interface for any given user (human, software process or device) to a configurable number of sessions. | A resource starvation DoS might occur if a limit is not imposed. There is a trade- off between potentially locking out a specific user versus locking out all users and services due to a lack of control system resources. Product supplier and/ or system integrator guidance is likely required to provide suffi cient information as to how the number of sessions value should be assigned. | The requirements for the four SL levels that relate to SR 2.7 – Concurrent session control are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: Not Selected • SL-C(UC, control system) 3: SR 2. 7 • SL-C(UC, control system) 4: SR 2. 7 | Same base identifier and enhancement sequence
30 | 2 | Base requirement | CR2.8 | CR 2.8 | CR | Auditable events | Component s shall provide the capability to generate audit records relevant to security for the following categories: a) access control; b) request errors; c) control system events; d) backup and restore event; e) configuration changes; and f) audit log events. Individual audit records shall include: a) timestamp; b) source (originating device, software process or human user account); c) category; d) type; e) event ID; and f) event result. | and supplemental guida nce Devices may contain either embedded firmware or run an OS. W hile t he intent of the requirement is to cover categories of events, at least all events from the above categories that can be generated by the firmware or OS are to be included. NOTE Security event categories are only applicable if functionality itself is provided by the component. | The requirements for the four security levels that relate to CR 2. 8 are: • SL-C(UC,component) 1: CR 2.8 • SL-C(UC,component) 2: CR 2.8 • SL-C(UC,component) 3: CR 2.8 • SL-C(UC,component) 4: CR 2.8 | SR2.8 | SR 2.8 | Auditable events | The control system shall provide the capability to generate audit records relevant to security for the following categories: access control, request errors, operating system events, control system events, backup and restore events, configuration changes, potential reconnaissance activity and audit log events. Individual audit records shall include the timestamp, source (originating device, software process or human user account), category, type, event ID and event result. | The purpose of this requirement is to record the occurrence of important events which need to be audited as significant and relevant to the security of the control system. Auditing activit y can affect control system performance. The security aud it function is usually coordinated with the network health and status monitoring function which may be in a different zone. Commonly recognized and accepted checklists and configuration guides should be considered when compili ng a list of auditable events. The security policies and procedures should define auditable events that are adequate to support after -the-fact investigations of security incidents. In addition, audit records should be sufficient to monitor the effectiveness and proper operation of the security mechanisms utilized to meet the requirements in this standard. It should be noted that the requirement for event recording is applicable within the given system functionality, specifically given system security requirements on a given level. For example, the requirement for recording of authentication events (in the access control category) on a SL 1 system is only applicable to the level of authentication functionality required for SL 1 according to the requirements in Clause 5. Events may occur in any control system component (for example login events) or may be observed by dedicated monitors. F or example, port scanning might be detected by an intrusion detection system (IDS) or intrusion prevention system (IPS). | The requirements for the four SL levels that relate to SR 2.8 – Auditable events are: • SL-C(UC, control system) 1: SR 2.8 • SL-C(UC, control system) 2: SR 2. 8 • SL-C(UC, control system) 3: SR 2. 8 (1) • SL-C(UC, control system) 4: SR 2. 8 (1) | Same base identifier and enhancement sequence
31 | 2 | Base requirement | CR2.9 | CR 2.9 | CR | Audit storage capacity | Component s shall a) provide the capability to allocate audit record storage capacity according to commonly recognized recommendations for log management; and b) provide mec hanisms to protect against a failure of the component when it reaches or exceeds the audit storage capacity. | Component s should provide sufficient audit storage capacity, and should consider retention policy, the auditing to be performed and the online audit processing requirements. Components may rely on the system into which they are integrated to provide the majority of audit storage capacity. However, the components should provide enough local storage to buffer audit data until it can be sent to the system. Guidelines to be considered may include NIST Spec ial Publication (SP) 800- 92 [19]. The audit storage capacity should be sufficient to retain logs for a period of time required by applicable policies and regulations or business requirements. | The requirements for the four SL levels that relate to CR 2.9 are: • SL-C(UC,component) 1: CR 2.9 • SL-C(UC,component) 2: CR 2.9 • SL-C(UC,component) 3: CR 2.9 (1) • SL-C(UC,component) 4: CR 2.9 (1) | SR2.9 | SR 2.9 | Audit storage capacity | The control system shall allocate sufficient audit record storage capacity according to commonly recognized recommendations for log management and system configuration. The control system shall provide auditing mechanisms to reduce the likelihood of such capacity being exceeded. | The control system should provide sufficient audit storage capacity, taking into account retention policy, the auditing to be performed and the online audit processing requirements. Guidelines to be considered could include the NIST Special Publication (SP) 800-92 [27]. The audit storage capacity should be sufficient to retain logs for a period of time required by applicable policies and regulations or business requirements. | The requirements for the four SL levels that relate to SR 2.9 – Audit storage capacity are: • SL-C(UC, control system) 1: SR 2.9 • SL-C(UC, control system) 2: SR 2.9 • SL-C(UC, control system) 3: SR 2.9 (1) • SL-C(UC, control system) 4: SR 2.9 (1) | Same base identifier and enhancement sequence
32 | 2 | Enhancement | CR2.9.1 | CR 2.9 RE (1) | CR | Warn when audit record storage capacity threshold reached | Component s shall provide the capability to issue a warning when the allocated audit record storage reaches a configurable threshold. | Component s should provide sufficient audit storage capacity, and should consider retention policy, the auditing to be performed and the online audit processing requirements. Components may rely on the system into which they are integrated to provide the majority of audit storage capacity. However, the components should provide enough local storage to buffer audit data until it can be sent to the system. Guidelines to be considered may include NIST Spec ial Publication (SP) 800- 92 [19]. The audit storage capacity should be sufficient to retain logs for a period of time required by applicable policies and regulations or business requirements. | The requirements for the four SL levels that relate to CR 2.9 are: • SL-C(UC,component) 1: CR 2.9 • SL-C(UC,component) 2: CR 2.9 • SL-C(UC,component) 3: CR 2.9 (1) • SL-C(UC,component) 4: CR 2.9 (1) | SR2.9.1 | SR 2.9 RE (1) | Warn when audit record storage capacity threshold reached | The control system shall provide the capability to issue a warning when the allocated audit record storage volume reaches a configurable percentage of maximu m audit record storage capacity. 6.11.3.2 Void | The control system should provide sufficient audit storage capacity, taking into account retention policy, the auditing to be performed and the online audit processing requirements. Guidelines to be considered could include the NIST Special Publication (SP) 800-92 [27]. The audit storage capacity should be sufficient to retain logs for a period of time required by applicable policies and regulations or business requirements. | The requirements for the four SL levels that relate to SR 2.9 – Audit storage capacity are: • SL-C(UC, control system) 1: SR 2.9 • SL-C(UC, control system) 2: SR 2.9 • SL-C(UC, control system) 3: SR 2.9 (1) • SL-C(UC, control system) 4: SR 2.9 (1) | Same base identifier and enhancement sequence
33 | 2 | Base requirement | CR2.10 | CR 2.10 | CR | Response to audit processing failures | Component s shall a) provide the capability to protect against the loss of essential services and functions in the event of an audit processing failure; and b) provide the capability to support appropriate actions in response to an audit processing failure according to commonly accepted industry practices and recommen dations. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | Audit generation typically occurs at the source of the event. Audit processing involves transmission, possible augmentation (such as, the addition of a timestamp) and persistent storage of the audit records. Aud it processing failures include, for example, software or hardware errors, failures in the audit capturing mechanisms and audit storage capacity being reached or exceeded. Guidelines to be considered when designing appropriate response actions may include t he NIST SP 800 -92, Guide to Computer Security Log Management [19]. It should be noted that either overwriting the oldest audit records or halting audit log generation are possible responses to audit storage capacity being exceeded but imply the loss of pote ntially essential forensic information. Also alerting personnel could be an appropriate supporting action in response to an audit processing failure. | The requirements for the four SL levels that relate to CR 2.10 are: • SL-C(UC,component) 1: CR 2.10 • SL-C(UC,component) 2: CR 2.10 • SL-C(UC,component) 3: CR 2.10 • SL-C(UC,component) 4: CR 2.10 | SR2.10 | SR 2.10 | Response to audit processing failures | The control system shall provide the capability to alert personnel and prevent the loss of essential services and functions in the event of an audit processing failure. The control system shall provide the capability to support appropriate actions in response to an audit processing failure according to commonly accepted industry practices and recommendations. | Audit generation typically occurs at the source of the event. Audit processing involves transmission, possible augmentation (such as the addition of a timestamp) and persistent storage of the audit records. Audit processing failures include, for example, software or hardware errors, failures in the audit capturing mechanisms and audit storage capac ity being reached or exceeded. Guidelines to be considered when designing appropriate response actions may include the NIST SP800 -92. It should be noted that either overwriting the oldest audit records or halting audit log generation are possible responses to audit storage capacity being exceeded but imply the loss of potentially essential forensic information. | The requirements for the four SL levels that relate to SR 2.10 – Response to audit processing failures are: • SL-C(UC, control system) 1: SR 2. 10 • SL-C(UC, control system) 2: SR 2. 10 • SL-C(UC, control system) 3: SR 2. 10 • SL-C(UC, control system) 4: SR 2. 10 | Same base identifier and enhancement sequence
34 | 2 | Base requirement | CR2.11 | CR 2.11 | CR | Timestamps | Component s shall provide the capability to create timestamps (including date and time) for use in audit records. | A good reference for the format of timestamps is ISO/IEC 8601:2004 [7]. Care should be taken when designing a system that periodic time -shift events, such as daylight savings time in some locations, are considered. | The requirements for the four security levels that relate to CR 2.11 are: • SL-C(UC,component) 1: CR 2.11 • SL-C(UC,component) 2: CR 2.11 (1) • SL-C(UC,component) 3: CR 2.11 (1) • SL-C(UC,component) 4: CR 2.11 (1) (2) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR2.11 | SR 2.11 | Timestamps | The control system shall provide timestamps for use in audit record generation. | Timestamps (including date and time) of audit records should be generated using internal system clocks. If system- wide time synchronization is not present (which is typical in many installations), known offsets would be needed to support analysis of a sequence of events. In addition, synchronization of internally generated audit records with external events might requ ire synchronization with a generally recognized external time source (such as the Global Positioning S ystem (GPS), Global Navigation Satellite System (GLONASS) and Galileo). The time source should be protected from unauthorized alteration. | The requirements for the four SL levels that relate to SR 2.11 – Timestamps are: • SL-C(UC, control system) 1: Not selected • SL-C(UC, control system) 2: SR 2. 11 • SL-C(UC, control system) 3: SR 2. 11 (1) • SL-C(UC, control system) 4: SR 2. 11 (1) (2) 6.14 SR 2.1 2 – Non-repudiation Requirement 6.14.1The control system shall provide the capability to determine whether a given human user took a particular action. Rationale and supplemental guidance 6.14.2 Examples of particular actions taken by a user include performing operator actions, changing control system configurations, creating information, sending a message, approving information (such as indicating concurre nce) and receiving a message. Non -repudiation protects against later false claims by a user of not having taken a specific action, by an author of not having authored a particular document, by a sender of not having transmitted a message, by a receiver of not having received a message or by a signatory of not having signed a document. Non- repudiation services can be used to determine if information originated from a user, if a user took specific actions (for example, sending an email and approving a work order) or received specific information. Non- repudiation services are obtained by employing various techniques or mechanisms (for ex ample, digital signatures, digital message receipts and timestamps). Requirement enhancements 6.14.3 6.14.3.1 SR 2.12 RE 1 – Non-repudiation for all users The control system shall provide the capability to determine whether a given user (human, software process or device) took a particular action. 6.14.3.2 Void Security levels 6.14.4 The requirements for the four SL levels that relate to SR 2.12 – Non-repudiation are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: Not Selected • SL-C(UC, control system) 3: SR 2.1 2 • SL-C(UC, control system) 4: SR 2.1 2 (1) 7 FR 3 – System integrity 7.1 Purpose and SL -C(SI) descriptions Ensure the integrity of the IACS to prevent unauthorized manipulation. • SL 1 – Protect the integrity of the IACS against casual or coincidental manipulation. • SL 2 – Protect the integrity of the IACS against manipulation by someone using simple means with low resources, generic skills and low motivation. • SL 3 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with extended resources, IACS specific skills and high motivation. 7.2 Rationale IACS often go through multiple testing cycles (unit testing, factory acceptance testing (FAT), site acceptance testing (S AT), certification, commissioning, etc.) to establish that the systems will perform as intended before they even begin production. Once operational, asset owners are responsible for maintaining the integrity of the IACS. Using their risk assessment methodo logy, asset owners may assign different levels of integrity protection to different systems, communication channels and information in their IACS. The integrity of physical assets should be maintained in both operational and non -operational states, such as during production, when in storage or during a maintenance shutdown. The integrity of logical assets should be maintained while in transit and at rest, such as being transmitted over a network or when residing in a data repository. | Same base identifier and enhancement sequence
35 | 2 | Enhancement | CR2.11.1 | CR 2.11 RE (1) | CR | Time synchronizati on | Component s shall provide the capability to create timestamps that are synchronized with a system wide time source. | A good reference for the format of timestamps is ISO/IEC 8601:2004 [7]. Care should be taken when designing a system that periodic time -shift events, such as daylight savings time in some locations, are considered. | The requirements for the four security levels that relate to CR 2.11 are: • SL-C(UC,component) 1: CR 2.11 • SL-C(UC,component) 2: CR 2.11 (1) • SL-C(UC,component) 3: CR 2.11 (1) • SL-C(UC,component) 4: CR 2.11 (1) (2) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR2.11.1 | SR 2.11 RE (1) | Internal time synchronization | The control system shall provide the capability to synchronize internal system clocks at a configurable frequency. | Timestamps (including date and time) of audit records should be generated using internal system clocks. If system- wide time synchronization is not present (which is typical in many installations), known offsets would be needed to support analysis of a sequence of events. In addition, synchronization of internally generated audit records with external events might requ ire synchronization with a generally recognized external time source (such as the Global Positioning S ystem (GPS), Global Navigation Satellite System (GLONASS) and Galileo). The time source should be protected from unauthorized alteration. | The requirements for the four SL levels that relate to SR 2.11 – Timestamps are: • SL-C(UC, control system) 1: Not selected • SL-C(UC, control system) 2: SR 2. 11 • SL-C(UC, control system) 3: SR 2. 11 (1) • SL-C(UC, control system) 4: SR 2. 11 (1) (2) 6.14 SR 2.1 2 – Non-repudiation Requirement 6.14.1The control system shall provide the capability to determine whether a given human user took a particular action. Rationale and supplemental guidance 6.14.2 Examples of particular actions taken by a user include performing operator actions, changing control system configurations, creating information, sending a message, approving information (such as indicating concurre nce) and receiving a message. Non -repudiation protects against later false claims by a user of not having taken a specific action, by an author of not having authored a particular document, by a sender of not having transmitted a message, by a receiver of not having received a message or by a signatory of not having signed a document. Non- repudiation services can be used to determine if information originated from a user, if a user took specific actions (for example, sending an email and approving a work order) or received specific information. Non- repudiation services are obtained by employing various techniques or mechanisms (for ex ample, digital signatures, digital message receipts and timestamps). Requirement enhancements 6.14.3 6.14.3.1 SR 2.12 RE 1 – Non-repudiation for all users The control system shall provide the capability to determine whether a given user (human, software process or device) took a particular action. 6.14.3.2 Void Security levels 6.14.4 The requirements for the four SL levels that relate to SR 2.12 – Non-repudiation are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: Not Selected • SL-C(UC, control system) 3: SR 2.1 2 • SL-C(UC, control system) 4: SR 2.1 2 (1) 7 FR 3 – System integrity 7.1 Purpose and SL -C(SI) descriptions Ensure the integrity of the IACS to prevent unauthorized manipulation. • SL 1 – Protect the integrity of the IACS against casual or coincidental manipulation. • SL 2 – Protect the integrity of the IACS against manipulation by someone using simple means with low resources, generic skills and low motivation. • SL 3 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with extended resources, IACS specific skills and high motivation. 7.2 Rationale IACS often go through multiple testing cycles (unit testing, factory acceptance testing (FAT), site acceptance testing (S AT), certification, commissioning, etc.) to establish that the systems will perform as intended before they even begin production. Once operational, asset owners are responsible for maintaining the integrity of the IACS. Using their risk assessment methodo logy, asset owners may assign different levels of integrity protection to different systems, communication channels and information in their IACS. The integrity of physical assets should be maintained in both operational and non -operational states, such as during production, when in storage or during a maintenance shutdown. The integrity of logical assets should be maintained while in transit and at rest, such as being transmitted over a network or when residing in a data repository. | Same base identifier and enhancement sequence
36 | 2 | Enhancement | CR2.11.2 | CR 2.11 RE (2) | CR | Protection of time source integrity | The time synchro nization mechanism shall provide the capability to detect unauthorized alteration and cause an audit event upon alteration. | A good reference for the format of timestamps is ISO/IEC 8601:2004 [7]. Care should be taken when designing a system that periodic time -shift events, such as daylight savings time in some locations, are considered. | The requirements for the four security levels that relate to CR 2.11 are: • SL-C(UC,component) 1: CR 2.11 • SL-C(UC,component) 2: CR 2.11 (1) • SL-C(UC,component) 3: CR 2.11 (1) • SL-C(UC,component) 4: CR 2.11 (1) (2) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR2.11.2 | SR 2.11 RE (2) | Protection of time source integrity | The time source shall be protected from unauthorized alteration and shall cause an audit event upon alteration. | Timestamps (including date and time) of audit records should be generated using internal system clocks. If system- wide time synchronization is not present (which is typical in many installations), known offsets would be needed to support analysis of a sequence of events. In addition, synchronization of internally generated audit records with external events might requ ire synchronization with a generally recognized external time source (such as the Global Positioning S ystem (GPS), Global Navigation Satellite System (GLONASS) and Galileo). The time source should be protected from unauthorized alteration. | The requirements for the four SL levels that relate to SR 2.11 – Timestamps are: • SL-C(UC, control system) 1: Not selected • SL-C(UC, control system) 2: SR 2. 11 • SL-C(UC, control system) 3: SR 2. 11 (1) • SL-C(UC, control system) 4: SR 2. 11 (1) (2) 6.14 SR 2.1 2 – Non-repudiation Requirement 6.14.1The control system shall provide the capability to determine whether a given human user took a particular action. Rationale and supplemental guidance 6.14.2 Examples of particular actions taken by a user include performing operator actions, changing control system configurations, creating information, sending a message, approving information (such as indicating concurre nce) and receiving a message. Non -repudiation protects against later false claims by a user of not having taken a specific action, by an author of not having authored a particular document, by a sender of not having transmitted a message, by a receiver of not having received a message or by a signatory of not having signed a document. Non- repudiation services can be used to determine if information originated from a user, if a user took specific actions (for example, sending an email and approving a work order) or received specific information. Non- repudiation services are obtained by employing various techniques or mechanisms (for ex ample, digital signatures, digital message receipts and timestamps). Requirement enhancements 6.14.3 6.14.3.1 SR 2.12 RE 1 – Non-repudiation for all users The control system shall provide the capability to determine whether a given user (human, software process or device) took a particular action. 6.14.3.2 Void Security levels 6.14.4 The requirements for the four SL levels that relate to SR 2.12 – Non-repudiation are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: Not Selected • SL-C(UC, control system) 3: SR 2.1 2 • SL-C(UC, control system) 4: SR 2.1 2 (1) 7 FR 3 – System integrity 7.1 Purpose and SL -C(SI) descriptions Ensure the integrity of the IACS to prevent unauthorized manipulation. • SL 1 – Protect the integrity of the IACS against casual or coincidental manipulation. • SL 2 – Protect the integrity of the IACS against manipulation by someone using simple means with low resources, generic skills and low motivation. • SL 3 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with extended resources, IACS specific skills and high motivation. 7.2 Rationale IACS often go through multiple testing cycles (unit testing, factory acceptance testing (FAT), site acceptance testing (S AT), certification, commissioning, etc.) to establish that the systems will perform as intended before they even begin production. Once operational, asset owners are responsible for maintaining the integrity of the IACS. Using their risk assessment methodo logy, asset owners may assign different levels of integrity protection to different systems, communication channels and information in their IACS. The integrity of physical assets should be maintained in both operational and non -operational states, such as during production, when in storage or during a maintenance shutdown. The integrity of logical assets should be maintained while in transit and at rest, such as being transmitted over a network or when residing in a data repository. | Same base identifier and enhancement sequence
37 | 2 | Base requirement | CR2.12 | CR 2.12 | CR | Non-repudiation | If a component provides a human user interface, the component shall provide the capability to determine whether a given human user took a particular action. Control elements that are not able to support such capability shall be l isted in component document s. | Examples of particular actions taken by a user include performing operator actions, changing control system configurations, creating information, sending a message, approving information (such as, indicating concurrence) and receiving a message. Non- repudiation protects against later false claims by a user of not having taken a specific action, by an author of not having authored a particular document, by a sender of not having transmitted a message, by a receiver of not having received a message or by a signatory of not having signed a document. Non- repudiation services can be used to determine if information originated from a user, if a user took specific actions (for example, sending an email and approving a work order) or received specific information. Non- repudiation services are obtained by employing various techniques or mechanisms (for example, user identification and authorization, digital signatures, digital message receipts and timestamps). | The requirements for the four SL levels that relate to CR 2. 12 are: • SL-C(UC,component) 1: CR 2.12 • SL-C(UC,component) 2: CR 2.12 • SL-C(UC,component) 3: CR 2.12 • SL-C(UC,component) 4: CR 2.12 (1) 6.15 CR 2.13 – Use of physical diagnostic and test interfaces The use of physical diagnostic and test interfaces requirements are component -specific and can be located as requirements for each specifi c component type in Clauses 12 through 15. 7 FR 3 – System integrity 7.1 Purpose and SL-C(SI) descriptions Ensure the integrity of the component to protect against unauthorized manipulation or modification. • SL 1 – Protect the integrity of the IACS against casual or coincidental manipulation. • SL 2 – Protect the integrity of the IACS against manipulation by someone using simple means with l ow resources, generic skills and low motivation. • SL 3 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with extended resources, IACS specific skills and high motivation. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 7.2 Rationale Component s often go through multiple testing cycles (unit testing, system testing, etc.) before they begin production to establish that the component s will perform as intended before they even begin production. Once operational, asset owners are responsible for maintaining the integrity of the component. Using their risk assessment methodology, asset owners may assign different levels of integrity protection to different components, communication channels and information in their IACS. The integrity of physical assets should be maintained in both operational and non- operational states, such as during production, when in storage or during a maintenance sh utdown. The integrity of logical assets should be maintained while in transit and at rest, such as being transmitted over a network or when residing in a data repository. | [6 empty] | No corresponding SR
38 | 2 | Enhancement | CR2.12.1 | CR 2.12 RE (1) | CR | Non-repudiation for all users | Component s shall provide the capability to determine whether a given user (human, software process or device) took a particular action. | Examples of particular actions taken by a user include performing operator actions, changing control system configurations, creating information, sending a message, approving information (such as, indicating concurrence) and receiving a message. Non- repudiation protects against later false claims by a user of not having taken a specific action, by an author of not having authored a particular document, by a sender of not having transmitted a message, by a receiver of not having received a message or by a signatory of not having signed a document. Non- repudiation services can be used to determine if information originated from a user, if a user took specific actions (for example, sending an email and approving a work order) or received specific information. Non- repudiation services are obtained by employing various techniques or mechanisms (for example, user identification and authorization, digital signatures, digital message receipts and timestamps). | The requirements for the four SL levels that relate to CR 2. 12 are: • SL-C(UC,component) 1: CR 2.12 • SL-C(UC,component) 2: CR 2.12 • SL-C(UC,component) 3: CR 2.12 • SL-C(UC,component) 4: CR 2.12 (1) 6.15 CR 2.13 – Use of physical diagnostic and test interfaces The use of physical diagnostic and test interfaces requirements are component -specific and can be located as requirements for each specifi c component type in Clauses 12 through 15. 7 FR 3 – System integrity 7.1 Purpose and SL-C(SI) descriptions Ensure the integrity of the component to protect against unauthorized manipulation or modification. • SL 1 – Protect the integrity of the IACS against casual or coincidental manipulation. • SL 2 – Protect the integrity of the IACS against manipulation by someone using simple means with l ow resources, generic skills and low motivation. • SL 3 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with extended resources, IACS specific skills and high motivation. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 7.2 Rationale Component s often go through multiple testing cycles (unit testing, system testing, etc.) before they begin production to establish that the component s will perform as intended before they even begin production. Once operational, asset owners are responsible for maintaining the integrity of the component. Using their risk assessment methodology, asset owners may assign different levels of integrity protection to different components, communication channels and information in their IACS. The integrity of physical assets should be maintained in both operational and non- operational states, such as during production, when in storage or during a maintenance sh utdown. The integrity of logical assets should be maintained while in transit and at rest, such as being transmitted over a network or when residing in a data repository. | [6 empty] | No corresponding SR
39 | 3 | Base requirement | CR3.1 | CR 3.1 | CR | Communication integrity | Component s shall provide the capability to protect integrity of transmitted information. | Many common network attacks are based on the manipulation of data in transmission, for example manipulation of network packets. Switched or routed networks provide a great er opportunity for attackers to manipulate packets as undetected access to these networks is generally easier and the switching and routing mechanisms themselves can also be manipulated in order to get more access to transmitted information. Manipulation in the context of a control system could include the change of measurement values communicated from a sensor to a receiver or the alteration of command parameters sent from a control application to an actuator. Depending on the context (for example transmi ssion within a local network segment versus transmission via untrusted networks) and the network type used in the transmission (for example transmission control protocol (TCP)/ Internet protocol (IP) versus local serial links), feasible and appropriate mechanisms will vary. On a small network with direct links (point -topoint), physical access protection to all nodes may be sufficient on lower SLs if the endpoints’ integrity is protected as well (see 7.6), while on a network distributed in areas with regular physical presence of staff or on a wide area network, physical access is likely not enforceable. If a commercial service is used to provide commun ication services as a commodity item rather than a fully dedicated service (for example a leased line versus a T1 link), it may be more difficult to obtain the necessary assurances regarding the implementation of needed security controls for communication integrity (for example because of legal restrictions). When it is infeasible or impractical to meet the necessary security requirements it may be appropriate to implement either appropriate compensating countermeasures or explicitly accept the additional r isk. Industrial equipment is often subject to environmental conditions that can lead to integrity issues and/or false positive incidents. T he environment often contains particulates, liquids, vibration, gases, radiation, and electromagnetic interference (EMI) that can cause conditions that affect the integrity of the communication wiring and signals. The network infrastructure should be designed to minimize these physical/environmental effects on communication integrity. For example, when particulate, liquids, and/or gases are an issue, it may be necessary to use a sealed registered jack 45 (RJ -45) or M12 connector instead of a commercial -grade RJ -45 connector on the wire. The cable itself may need to use a different jacket instead to handle the particulate, liquid, and/or gas as well. In cases where vibration is an issue, M12 connectors may be necessary to prevent the spring pins on an RJ -45 connector from disconnecting during use. In cases where radiation and/or EMI are an issue, it may be necessary to use shielded twisted pair or fiber cables to prevent any effect on the communication signals. It may also be necessary to perform a wireless spectrum analysis in these areas if wireless networking is planned to verify that it is a viable solution. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | The requirements for the four SL levels that relate to CR 3.1 are: • SL-C(SI, component) 1: CR 3.1 • SL-C(SI, component) 2: CR 3.1 (1) • SL-C(SI, component) 3: CR 3.1 (1) • SL-C(SI, component) 4: CR 3.1 (1) 7.4 CR 3.2 – Protection from malicious code The protection from malicious code requirements are component -specific and can be located as requirements for each specific component type in Clauses 12 through 15. | SR3.1 | SR 3.1 | Communication integrity | The control system shall provide the capability to protect the integrity of transmitted information. | Many common network attacks are based on the manipulation of data in transmission, for example manipulation of network packets. Switched or routed networks provide a greater opportunity for attackers to manipulate packets as undetected access to these networks is generally easier and the switching and routing mechanisms themselves can also be manipulated in order to get more access to transmitted information. Manipulation in the context of a control system could include the change of measurement values communicated from a sensor to a receiver or the alteration of command parameters sent from a contr ol application to an actuator. Depending on the context (for example transmission within a local network segment versus transmission via untrusted networks) and the network type used in the transmission (for example transmission control protocol (TCP) / internet protocol (IP) versus local serial links), feasible and appropriate mechanisms will vary. On a small network with direct links (point -topoint), physical access protection to all nodes may be sufficient on lower SLs if the endpoints’ integrity is pro tected as well (see 7.6, SR 3.4 – Software and information integrity), while on a network distributed in areas with regular physical presence of staff or on a wide area network physical access is likely not enforceable. If a commercial service is used to provide communication services as a commodity item rather than a fully dedicated service (for example a leased line v ersus a T1 link), it may be more difficult to obtain the necessary assurances regarding the implementation of needed security controls for communication integrity (for example because of legal restrictions). When it is infeasible or impractical to meet the necessary security requirements it may be appropriate to implement either appropriate compensating countermeasures or explicitly accept the additional risk. Industrial equipment is often subject to environmental conditions that can lead to integrity issues and/or false positive incidents. Many times the environment contains particulates, liquids, vibration, gases, radiation, and electromagnetic interference (EMI) that can cause conditions that affect the integrity of the communication wiring and signals. The network infrastructure should be designed to minimize these physical/environmental effects on communication integrity. For example, when particulate, liquids, and/or gases are an issue, it may be necessary to use a sealed registered jack 45 (RJ -45) or M12 connector instead of a commercial -grade RJ -45 connector on the wire. The cable itself may need to use a different jacket instead to handle the particulate, liquid, and/or gas as well. In cases where vibration is an issue, M12 connectors may be necessary to prevent the spring pins on an RJ -45 connector from disconnecting during use. In cases where radiation and/or EMI are an issue, it may be necessary to use shielded twisted pair or fiber cables to prevent any effect on the communication signals. It may also be necessary to perform a wireless spectrum analysis in these areas if wireless networking is planned to verify that it is a viable solution. | The requirements for the four SL levels that relate to SR 3.1 – Communication integrity are: • SL-C(S I, contr ol system) 1: SR 3.1 • SL-C(SI, control system) 2: SR 3.1 • SL-C(SI, control system) 3: SR 3.1 (1) • SL-C(SI, control system) 4: SR 3.1 (1) | Same base identifier and enhancement sequence
40 | 3 | Enhancement | CR3.1.1 | CR 3.1 RE (1) | CR | Communication authentication | Component s shall provide the capability to verify the authenticity of received information during communication. NOTE Both integrity protection and authentication of origin can be achieved without providing confidentiality protection. | Many common network attacks are based on the manipulation of data in transmission, for example manipulation of network packets. Switched or routed networks provide a great er opportunity for attackers to manipulate packets as undetected access to these networks is generally easier and the switching and routing mechanisms themselves can also be manipulated in order to get more access to transmitted information. Manipulation in the context of a control system could include the change of measurement values communicated from a sensor to a receiver or the alteration of command parameters sent from a control application to an actuator. Depending on the context (for example transmi ssion within a local network segment versus transmission via untrusted networks) and the network type used in the transmission (for example transmission control protocol (TCP)/ Internet protocol (IP) versus local serial links), feasible and appropriate mechanisms will vary. On a small network with direct links (point -topoint), physical access protection to all nodes may be sufficient on lower SLs if the endpoints’ integrity is protected as well (see 7.6), while on a network distributed in areas with regular physical presence of staff or on a wide area network, physical access is likely not enforceable. If a commercial service is used to provide commun ication services as a commodity item rather than a fully dedicated service (for example a leased line versus a T1 link), it may be more difficult to obtain the necessary assurances regarding the implementation of needed security controls for communication integrity (for example because of legal restrictions). When it is infeasible or impractical to meet the necessary security requirements it may be appropriate to implement either appropriate compensating countermeasures or explicitly accept the additional r isk. Industrial equipment is often subject to environmental conditions that can lead to integrity issues and/or false positive incidents. T he environment often contains particulates, liquids, vibration, gases, radiation, and electromagnetic interference (EMI) that can cause conditions that affect the integrity of the communication wiring and signals. The network infrastructure should be designed to minimize these physical/environmental effects on communication integrity. For example, when particulate, liquids, and/or gases are an issue, it may be necessary to use a sealed registered jack 45 (RJ -45) or M12 connector instead of a commercial -grade RJ -45 connector on the wire. The cable itself may need to use a different jacket instead to handle the particulate, liquid, and/or gas as well. In cases where vibration is an issue, M12 connectors may be necessary to prevent the spring pins on an RJ -45 connector from disconnecting during use. In cases where radiation and/or EMI are an issue, it may be necessary to use shielded twisted pair or fiber cables to prevent any effect on the communication signals. It may also be necessary to perform a wireless spectrum analysis in these areas if wireless networking is planned to verify that it is a viable solution. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | The requirements for the four SL levels that relate to CR 3.1 are: • SL-C(SI, component) 1: CR 3.1 • SL-C(SI, component) 2: CR 3.1 (1) • SL-C(SI, component) 3: CR 3.1 (1) • SL-C(SI, component) 4: CR 3.1 (1) 7.4 CR 3.2 – Protection from malicious code The protection from malicious code requirements are component -specific and can be located as requirements for each specific component type in Clauses 12 through 15. | SR3.1.1 | SR 3.1 RE (1) | Cryptographic integrity protection | The control system shall provide the capability to employ cryptographic mechanisms to recognize changes to information during communication. NOTE It is a commonly accepted good practice to determine the appropriate use of cryptographic mechanisms for message authentication and integrity after careful consideration of the security needs and the potential ramifications on system performance and capability to recover from system failure. 7.3.3.2 Void | Many common network attacks are based on the manipulation of data in transmission, for example manipulation of network packets. Switched or routed networks provide a greater opportunity for attackers to manipulate packets as undetected access to these networks is generally easier and the switching and routing mechanisms themselves can also be manipulated in order to get more access to transmitted information. Manipulation in the context of a control system could include the change of measurement values communicated from a sensor to a receiver or the alteration of command parameters sent from a contr ol application to an actuator. Depending on the context (for example transmission within a local network segment versus transmission via untrusted networks) and the network type used in the transmission (for example transmission control protocol (TCP) / internet protocol (IP) versus local serial links), feasible and appropriate mechanisms will vary. On a small network with direct links (point -topoint), physical access protection to all nodes may be sufficient on lower SLs if the endpoints’ integrity is pro tected as well (see 7.6, SR 3.4 – Software and information integrity), while on a network distributed in areas with regular physical presence of staff or on a wide area network physical access is likely not enforceable. If a commercial service is used to provide communication services as a commodity item rather than a fully dedicated service (for example a leased line v ersus a T1 link), it may be more difficult to obtain the necessary assurances regarding the implementation of needed security controls for communication integrity (for example because of legal restrictions). When it is infeasible or impractical to meet the necessary security requirements it may be appropriate to implement either appropriate compensating countermeasures or explicitly accept the additional risk. Industrial equipment is often subject to environmental conditions that can lead to integrity issues and/or false positive incidents. Many times the environment contains particulates, liquids, vibration, gases, radiation, and electromagnetic interference (EMI) that can cause conditions that affect the integrity of the communication wiring and signals. The network infrastructure should be designed to minimize these physical/environmental effects on communication integrity. For example, when particulate, liquids, and/or gases are an issue, it may be necessary to use a sealed registered jack 45 (RJ -45) or M12 connector instead of a commercial -grade RJ -45 connector on the wire. The cable itself may need to use a different jacket instead to handle the particulate, liquid, and/or gas as well. In cases where vibration is an issue, M12 connectors may be necessary to prevent the spring pins on an RJ -45 connector from disconnecting during use. In cases where radiation and/or EMI are an issue, it may be necessary to use shielded twisted pair or fiber cables to prevent any effect on the communication signals. It may also be necessary to perform a wireless spectrum analysis in these areas if wireless networking is planned to verify that it is a viable solution. | The requirements for the four SL levels that relate to SR 3.1 – Communication integrity are: • SL-C(S I, contr ol system) 1: SR 3.1 • SL-C(SI, control system) 2: SR 3.1 • SL-C(SI, control system) 3: SR 3.1 (1) • SL-C(SI, control system) 4: SR 3.1 (1) | Same base identifier and enhancement sequence
41 | 3 | Base requirement | CR3.3 | CR 3.3 | CR | Security functionality verification | Components shall provide the capability to support verif ication of the intended operation of security functions according to IEC 62443 -3-3 SR3.3. | The product supplier and/or system integrator should provide guidance on how to test the designed security controls. Asset owners need to be aware of the possible ramifications of running these verification tests during normal operations. Details of the execution of these verifications need to be specified with careful consideration of the requirements for continuous operations (for example, scheduling or prior notification). Examples of security verification functions include: • Verification of antivirus countermeasures by European Institute for Computer Antivirus Research (EICAR) testing of the control system file system. Antivirus software should detect the EICAR test samples and appropriate incident handling procedures should be triggered. • Verification of the identification, authentication and use control countermeasures by attempting access with an unauthorized account (for some functionality this could be automated). • Verification of intrusion detection systems (IDSs) as a security control by including a rule in the IDS that triggers on irregular, but known non -malicious traffic. The test could then be performed by introducing traffic that triggers this rule and the appropriate IDS monitoring and incident handling procedures. • Confirmation that audit logging is occurring as required by security policies and procedures and has not been disabled by an internal or external entity. | The requirements for the four SL levels that relate to CR 3.3 are: • SL-C(SI, component) 1: CR 3.3 • SL-C(SI, component) 2: CR 3.3 • SL-C(SI, component) 3: CR 3.3 • SL-C(SI, component) 4: CR 3.3 (1) | SR3.3 | SR 3.3 | Security functionality verification | The control system shall provide the capability to support verification of the intended operation of security functions and report when anomalies are discovered during FAT, SAT and scheduled maintenance. These securit y functions shall include all those necessary to support the security requirements specified in this standard. | The product supplier and/or system integrator should provide guidance on how to test the designed security co ntrols. Asset owners need to be aware of the possible ramifications of running these verification tests during normal operations. Details of the execution of these verifications need to be specified with careful consideration of the requirements for contin uous operations (for example, scheduling or prior notification). Examples of security verification functions include: • Verification of antivirus measures by European Institute for Computer Antivirus Research (EICAR) testing of the control system file system. Antivirus software should detect this and appropriate incident handling procedures should be triggered. • Verification of the identification, authentication and use control measures by attempting access with an unauthorized account (for some functionality this could be automated). • Verification of IDSs as a security control by including a rule in the IDS that triggers on irregular, but known non -malicious traffic. The test could then be performed by introducing traffic that triggers this rule and the appropriate IDS monitoring and incident handling procedures. • Confirm ation that audit logging is occurring as required by security policies and procedures and has not been disabled by an internal or external entity. | The requirements for the four SL levels that relate to SR 3.3 – Security functionality verification are: • SL-C(SI, control system) 1: SR 3.3 • SL-C(SI, control system) 2: SR 3.3 • SL-C(SI, control system) 3: SR 3.3 (1) • SL-C(SI, control system) 4: SR 3.3 (1) (2) | Same base identifier and enhancement sequence
42 | 3 | Enhancement | CR3.3.1 | CR 3.3 RE (1) | CR | Security functionality verification during normal operation | Component s shall provide the capability to support verification of the intended operation of security functions during normal operations. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 This RE needs to be carefully implemented to avoid detrimental effects. It may not be suitable for safety systems. | The product supplier and/or system integrator should provide guidance on how to test the designed security controls. Asset owners need to be aware of the possible ramifications of running these verification tests during normal operations. Details of the execution of these verifications need to be specified with careful consideration of the requirements for continuous operations (for example, scheduling or prior notification). Examples of security verification functions include: • Verification of antivirus countermeasures by European Institute for Computer Antivirus Research (EICAR) testing of the control system file system. Antivirus software should detect the EICAR test samples and appropriate incident handling procedures should be triggered. • Verification of the identification, authentication and use control countermeasures by attempting access with an unauthorized account (for some functionality this could be automated). • Verification of intrusion detection systems (IDSs) as a security control by including a rule in the IDS that triggers on irregular, but known non -malicious traffic. The test could then be performed by introducing traffic that triggers this rule and the appropriate IDS monitoring and incident handling procedures. • Confirmation that audit logging is occurring as required by security policies and procedures and has not been disabled by an internal or external entity. | The requirements for the four SL levels that relate to CR 3.3 are: • SL-C(SI, component) 1: CR 3.3 • SL-C(SI, component) 2: CR 3.3 • SL-C(SI, component) 3: CR 3.3 • SL-C(SI, component) 4: CR 3.3 (1) | SR3.3.1 | SR 3.3 RE (1) | Automated mechanisms for security functionality verification | The control system shall provide the capability to employ automated mechanisms to support management of security verification during FAT, SAT and scheduled maintenance. | The product supplier and/or system integrator should provide guidance on how to test the designed security co ntrols. Asset owners need to be aware of the possible ramifications of running these verification tests during normal operations. Details of the execution of these verifications need to be specified with careful consideration of the requirements for contin uous operations (for example, scheduling or prior notification). Examples of security verification functions include: • Verification of antivirus measures by European Institute for Computer Antivirus Research (EICAR) testing of the control system file system. Antivirus software should detect this and appropriate incident handling procedures should be triggered. • Verification of the identification, authentication and use control measures by attempting access with an unauthorized account (for some functionality this could be automated). • Verification of IDSs as a security control by including a rule in the IDS that triggers on irregular, but known non -malicious traffic. The test could then be performed by introducing traffic that triggers this rule and the appropriate IDS monitoring and incident handling procedures. • Confirm ation that audit logging is occurring as required by security policies and procedures and has not been disabled by an internal or external entity. | The requirements for the four SL levels that relate to SR 3.3 – Security functionality verification are: • SL-C(SI, control system) 1: SR 3.3 • SL-C(SI, control system) 2: SR 3.3 • SL-C(SI, control system) 3: SR 3.3 (1) • SL-C(SI, control system) 4: SR 3.3 (1) (2) | Same base identifier and enhancement sequence
43 | 3 | Base requirement | CR3.4 | CR 3.4 | CR | Software and information integrity | Component s shall provide the capability to perform or support integrity checks on software, configuration and other information as well as the recording and reporting of the results of these checks or be integrated into a system that can perfor m or support integrity checks. | Integrity verification methods are employed to detect, record, report and protect against software and information tampering that may occur if other protection mechanisms (such as authoriza tion enforcement) have been circumvented. Components should employ formal or recommended integrity mechanisms (such as cryptographic hashes). For example, such mechanisms could be used to monitor field devices for their latest configuration information to detect security breaches (including unauthorized changes). | The requirements for the four SL levels that relate to CR 3.4 are: • SL-C(SI, component) 1: CR 3.4 • SL-C(SI, component) 2: CR 3.4 (1) • SL-C(SI, component) 3: CR 3.4 (1) (2) • SL-C(SI, component) 4: CR 3.4 (1) (2) | SR3.4 | SR 3.4 | Software and information integrity | The control system shall provide the capability to detect, record, report and protect against unauthorized change s to software and information at rest. | Unauthorized changes are changes for which the entity attempting the change does not have the required privileges. This SR complements related SRs from FRs 1 and 2. FRs 1 and 2 involve enforcing the roles, privileges and use patterns as designed. Integrity verification methods are employed to detect, record, report and protect against software and information tampering that may occur if other protection mechanisms (such as authorization enforcement) have been circumvented. The control system should employ formal or recommended integrity mechanisms (such as cryptographic hashes). For example, such mechanisms could be used to monitor field devices for their latest configuration information to detect security breaches (including unauthorized changes). | The requirements for the four SL levels that relate to SR 3.4 – Software and information integrity are:  SL-C(SI, control system) 1: Not selected  SL-C(SI, control system) 2: SR 3.4  SL-C(SI, control system) 3: SR 3.4 (1)  SL-C(SI, control system) 4: SR 3.4 (1) | Same base identifier and enhancement sequence
44 | 3 | Enhancement | CR3.4.1 | CR 3.4 RE (1) | CR | Authenticity of software and information | Component s shall provide the capability to perform or support authenticity checks on software, configuration and other informat ion as well as the recording and reporting of the results of these checks or be integrated into a system that can perform or support authenticity checks. | Integrity verification methods are employed to detect, record, report and protect against software and information tampering that may occur if other protection mechanisms (such as authoriza tion enforcement) have been circumvented. Components should employ formal or recommended integrity mechanisms (such as cryptographic hashes). For example, such mechanisms could be used to monitor field devices for their latest configuration information to detect security breaches (including unauthorized changes). | The requirements for the four SL levels that relate to CR 3.4 are: • SL-C(SI, component) 1: CR 3.4 • SL-C(SI, component) 2: CR 3.4 (1) • SL-C(SI, component) 3: CR 3.4 (1) (2) • SL-C(SI, component) 4: CR 3.4 (1) (2) | SR3.4.1 | SR 3.4 RE (1) | Automated notification about integrity violations | The control system shall provide the capability to use automated tools that provide notification to a configurable set of recipients upon discovering discrepancies during integrity verification. 7.6.3.2 Void | Unauthorized changes are changes for which the entity attempting the change does not have the required privileges. This SR complements related SRs from FRs 1 and 2. FRs 1 and 2 involve enforcing the roles, privileges and use patterns as designed. Integrity verification methods are employed to detect, record, report and protect against software and information tampering that may occur if other protection mechanisms (such as authorization enforcement) have been circumvented. The control system should employ formal or recommended integrity mechanisms (such as cryptographic hashes). For example, such mechanisms could be used to monitor field devices for their latest configuration information to detect security breaches (including unauthorized changes). | The requirements for the four SL levels that relate to SR 3.4 – Software and information integrity are:  SL-C(SI, control system) 1: Not selected  SL-C(SI, control system) 2: SR 3.4  SL-C(SI, control system) 3: SR 3.4 (1)  SL-C(SI, control system) 4: SR 3.4 (1) | Same base identifier and enhancement sequence
45 | 3 | Enhancement | CR3.4.2 | CR 3.4 RE (2) | CR | Automated notification of integrity violations | If the component is performing the integrity check, it shall be capable of automatically providing notification to a configurable entity upon discovery of an attempt to make an unauthorized change. | Integrity verification methods are employed to detect, record, report and protect against software and information tampering that may occur if other protection mechanisms (such as authoriza tion enforcement) have been circumvented. Components should employ formal or recommended integrity mechanisms (such as cryptographic hashes). For example, such mechanisms could be used to monitor field devices for their latest configuration information to detect security breaches (including unauthorized changes). | The requirements for the four SL levels that relate to CR 3.4 are: • SL-C(SI, component) 1: CR 3.4 • SL-C(SI, component) 2: CR 3.4 (1) • SL-C(SI, component) 3: CR 3.4 (1) (2) • SL-C(SI, component) 4: CR 3.4 (1) (2) | [6 empty] | No corresponding SR
46 | 3 | Base requirement | CR3.5 | CR 3.5 | CR | Input validation | Component s shall validate the syntax, length and content of any input data that is used as an industrial process control input or input via external interfaces that directly impacts the action of the component. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | Rules for checking the valid syntax of input data such as set points should be in place to verify that this information has not been tampered with and conforms to the specification. Inputs passed to interpreters should be pre -screened to prevent the content from being unintentionally interpreted as commands. Note that this is a security CR, thus it does not address human error, for example supplying a legitimate integer number which is outside the expected range. Generally accepted industry practices for input data validation include out -of-range values for a defined field type, invalid characters in data fields, missing or incomplete data and buffer overflow. Additional examples where invalid inputs lead to system security issues include SQL injection attacks, cross- site scripting or malformed packets (as commonly generated by protocol fuzzers). Guidelines to be considered should include well-know n guidelines such as the Open Web Application Security Project (OWASP) Code Review Guide [21]. | The requirements for the four SL levels that relate to CR 3.5 are: • SL-C(SI, component) 1: CR 3.5 • SL-C(SI, component) 2: CR 3.5 • SL-C(SI, component) 3: CR 3.5 • SL-C(SI, component) 4: CR 3.5 | SR3.5 | SR 3.5 | Input validation | The control system shall validate the syntax and content of any input which is used as an industrial process control input or input that directly impacts the action of the control system. | Rules for checking the valid syntax of control system inputs such as set points should be in place to verify that this information has not been tampered with and is compliant with the specification. Inputs passed to interpreters should be pre-screened to prevent the content from being unintentionally interpreted as commands. Note that this is a security SR, thus it does not address human error, for example supplying a legitimate integer number which is outside the expected range. Generally accepted industry practices for input data validation include out-of-range values for a defined field type, invalid characters in data fields, missing or incomplete data and buffer overflow. Additional examples where invalid inputs lead to system security issues include SQL injection attacks, cross-site scripting or ma lformed packets (as commonly generated by protocol fuzzers). Guidelines to be considered could include the Open Web Application Security Project (OWASP) [31] Code Review Guide. | The requirements for the four SL levels that relate to SR 3.5 – Input validation are:  SL-C(SI, control system) 1: SR 3.5  SL-C(SI, control system) 2: SR 3.5  SL-C(SI, control system) 3: SR 3.5  SL-C(SI, control system) 4: SR 3.5 | Same base identifier and enhancement sequence
47 | 3 | Base requirement | CR3.6 | CR 3.6 | CR | Deterministic output | Components that physically or logically connect to an automation process shall provide the capability to set outputs to a predetermined state if normal operat ion as defined by the component supplier cannot be maintained. | The deterministic behaviou r of control system outputs as a result of threat actions against the control system devices and software is an important characteristic to ensure the integrity of normal operations. Ideally, the device continues to operate normally while under attack, but if the control system cannot maintain normal operation, then the control system outputs need to fail to a predetermined state. The appropriate predetermined state of control system outputs is device dependent and could be one of the following user configurable options: • Unpowered – the outputs fail to the unpowered state; • Hold – the outputs fail to the last -known good value; or • Fixed – the outputs fail to a fixed value that is determined by the asset owner or an application; or • Dynamic – the outputs fail to one of the above options based on the current state. | The requirements for the four SL levels that relate to CR 3.6 are: • SL-C(SI, component) 1: CR 3.6 • SL-C(SI, component) 2: CR 3.6 • SL-C(SI, component) 3: CR 3.6 • SL-C(SI, component) 4: CR 3.6 | SR3.6 | SR 3.6 | Deterministic output | The control system shall provide the capability to set outputs to a predetermined state if normal operation cannot be maintained as a result of an attack. | The deterministic behavior of control system outputs as a result of threat actions against the control system is an important characteristic to ensure the integrity of normal operations. Ideally, the control system continues to operate normally while under attack, but if the control system cannot maintain normal operation, then the control system outputs need to fail to a predetermined state. The appropriate predetermined state of control system outputs is application dependent and could be one of the following user configurable options: • Unpowered – the outputs fail to the unpowered state • Hold – the outputs fail to the last -known good value • Fixed – the outputs fail to a fixed value that is determined by the asset owner or an application | The requirements for the four SL levels that relate to SR 3.6 – Deterministic output are: • SR-C(SI, control system) 1: SR 3.6 • SR-C(SI, control system) 2: SR 3.6 • SR-C(SI, control system) 3: SR 3.6 • SR-C(SI, control system) 4: SR 3.6 | Same base identifier and enhancement sequence
48 | 3 | Base requirement | CR3.7 | CR 3.7 | CR | Error handling | Component s shall identify and handle error conditions in a manner that does not provide information that could be exploited by adversaries to attack the IACS. | The product supplier and/or system integrator should carefully consider the structure and content of error messages. Error messages generated by the component should provide timely and useful information without revealing potentially harmful information that could be used by adversaries to exploit the IACS. Disclosure of this information should be justified by the necessity for timely resolution of error conditions. Guidelines to be considered could include well-know n guidelines such as the OWASP Code Review Guide. A good example of an error message that could help adversaries attack an IACS would be to provide details of why authentication with the system failed. For example, stating invalid user or invalid password in the feedback would help an adversary attack the IACS and thus should not be provided. |  | SR3.7 | SR 3.7 | Error handling | The control system shall identify and handle error conditions in a manner such that effective remediation can occur. This shall be done in a manner which does not provide information that could be exploited by adversaries to attack the IACS unless revealing this information is necessary for the timely troubleshooting of problems. | The structure and content of error messages should be carefully considered by the product supplier and/or syste m integrator. Error messages generated by the control system should provide timely and useful information without revealing potentially harmful inform ation that could be used by adversaries to exploit the IACS. Since it may be unclear whether a particular error condition is due to a security event, all error messages may need to be easily accessible during incident response. Disclosure of this information should be justified by the necessity for timely resolution of error conditions. Guidelines to be considered could include the OWASP Code Review Guide [31]. | The requirements for the four SL levels that relat e to SR 3.7 – Error handling are: • SL-C(SI, control system) 1: Not Selected • SL-C(SI, control system) 2: SR 3. 7 • SL-C(SI, control system) 3: SR 3.7 • SL-C(SI, control system) 4: SR 3. 7 | Same base identifier and enhancement sequence
49 | 3 | Base requirement | CR3.8 | CR 3.8 | CR | Session integrity | Component s shall provide mechanisms to protect the integrity of communications sessions including: a) the capability to invalidate session identifiers upon user logout or other session termination (including browser sessions); b) the capability to generate a unique session iden tifier for each session and recognize only session identifiers that are system -generated; and c) the capability to generate unique session identifiers with commonly accepted sources of randomness. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | This control focuses on co mmunications protection at the session, versus packet, level. The intent of this control is to establish grounds for confidence at each end of a communications session in the ongoing identity of the other party and in the validity of the information being transmitted. For example, this control addresses man- in-the-middle attacks including session hijacking, insertion of false information into a session or replay attacks. Use of session integrity mechanisms can have a significant overhead and therefore their use should be considered in light of requirements for real -time communications. Session hijacking and other man- in-the-middle attacks or injections of false information often take advantage of easy -to-guess session IDs (keys or other shared secrets) or use of session IDs that were not properly invalidated after session termination. Therefore the validity of a session authenticator should be tightly connected to the lifetime of a session. Employing randomness in the generation of unique session IDs helps t o protect against brute- force attacks to determine future session IDs. | The requirements for the four SL levels that relate to CR 3.8 are: • SL-C(SI, component) 1: Not selected • SL-C(SI, component) 2: CR 3.8 • SL-C(SI, component) 3: CR 3.8 • SL-C(SI, component) 4: CR 3.8 | SR3.8 | SR 3.8 | Session integrity | The control system shall provide the capability to protect the integrity of sessions. The control system shall reject any usage of invalid session IDs. | This control focuses on communications protection at the session, versus packet, level. The intent of this control is to establish grounds for confidence at each end of a communications session in the ongoing identity of the other party and in the validity of the information being transmitted. For example, this control addresses man- in-the-middle attacks including session hijacking, insertion of false information into a session or replay attacks. Use of session integrity mechanisms can have a significant overhead and therefore their use should be considered in light of requirements for real-time communications. | The requirements for the four SL levels that relate to SR 3.8 – Session integrity are: • SL-C(SI, control system) 1: Not Selected • SL-C(SI, control system) 2: SR 3. 8 • SL-C(SI, control system) 3: SR 3. 8 (1) (2) • SL-C(SI, control system) 4: SR 3. 8 (1) (2) (3) | Same base identifier and enhancement sequence
50 | 3 | Base requirement | CR3.9 | CR 3.9 | CR | Protection of audit information | Components shall protect audit information, audit logs, and audit tools (if present) from unauthorized access, modification and deletion. 7.11.2 Rational e and supplemental guidance Audit information includes all information (for example, audit records, audit settings and audit reports) needed to successfully audit control system activity. The audit information is important for error correction, security br each recovery, investigations and related efforts. Mechanisms for enhanced protection against modification and deletion include the storage of audit information to hardware- enforced write- once media. | Some component -generated information, whether at rest or in transit, is of a confidential or sensitive nature. This implies that some communication channels and datastores require protection against eavesdropping and unauthorized access. | The requirements for the four SL levels that relate to CR 3. 9 are: • SL-C(SI, component) 1: Not selected • SL-C(SI, component) 2: CR 3.9 • SL-C(SI, component) 3: CR 3.9 • SL-C(SI, component) 4: CR 3.9 (1) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 7.12 CR 3.10 – Support for updates The support for updates requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15. 7.13 CR 3.11 – Physical tamper resistance and detection The physical tamper resistance and detection requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15. 7.14 CR 3.12 – Provisioning product supplier roots of trust The provisioning product supplier r oots of trust requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15. 7.15 CR 3.13 – Provisioning asset owner roots of trust The provisioning asset owner roots of trust requirements are component -specific and can be located as r equirements for each specific device type in Clauses 12 through 15. 7.16 CR 3.14 – Integrity of the boot process The integrity of the boot proc ess requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15. 8 FR 4 – Data confidentiality 8.1 Purpose and SL-C(DC) descriptions Ensure the confidentiality of information on communication channels and in data stored in repositories to protect against unauthorized disclosure. • SL 1 – Prevent the unauthorized disclosure of information via eavesdropping or casual exposure. • SL 2 – Prevent the unauthorized disclosure of information to an entity actively searching for it using simple means with low resources, generic skills and low motivation. • SL 3 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with extended resources, IACS specific skills and high motivation. | SR3.9 | SR 3.9 | Protection of audit information | The control system shall protect audit information and audit tools (if present) from unauthorized access, modification and deletion. | Audit information includes all information (for example, audit records, audit settings and audit reports) needed to successfully audit control system activity. The audit information is important for error correction, security breach recovery, investigations and related efforts. Mechanisms for enhanced protection against modification and deletion include the storage of audit information to hardware- enforced write- once media. | The requirements for the four SL levels that relate to SR 3.9 – Protection of audit information are: • SL-C(SI, control system) 1: Not selected • SL-C(SI, control system) 2: SR 3.9 • SL-C(SI, control system) 3: SR 3.9 • SL-C(SI, control system) 4: SR 3.9 (1) 8 FR 4 – Data confidentiality 8.1 Purpose and SL-C(DC) descriptions Ensure the confidentiality of information on communication channels and in data repositories to prevent unauthorized disclosure. • SL 1 – Prevent the unauthorized disclosure of information via eavesdropping or casual exposure. • SL 2 – Prevent the unauthorized disclosure of information to an entity actively searching for it using simple means with low resources, generic skills and low motivation. • SL 3 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with extended resources, IACS specific skills and high motivation. 8.2 Rationale Some control system -generated information, whether at rest or in transit, is of a confidential or sensitive na ture. This implies that some communication channels and data- stores require protection against eavesdr opping and unauthorized access. | Same base identifier and enhancement sequence
51 | 3 | Enhancement | CR3.9.1 | CR 3.9 RE (1) | CR | Audit records on write -once media | Components shall provide the capability to store audit records on hardware- enforced write -once media. | Some component -generated information, whether at rest or in transit, is of a confidential or sensitive nature. This implies that some communication channels and datastores require protection against eavesdropping and unauthorized access. | The requirements for the four SL levels that relate to CR 3. 9 are: • SL-C(SI, component) 1: Not selected • SL-C(SI, component) 2: CR 3.9 • SL-C(SI, component) 3: CR 3.9 • SL-C(SI, component) 4: CR 3.9 (1) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 7.12 CR 3.10 – Support for updates The support for updates requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15. 7.13 CR 3.11 – Physical tamper resistance and detection The physical tamper resistance and detection requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15. 7.14 CR 3.12 – Provisioning product supplier roots of trust The provisioning product supplier r oots of trust requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15. 7.15 CR 3.13 – Provisioning asset owner roots of trust The provisioning asset owner roots of trust requirements are component -specific and can be located as r equirements for each specific device type in Clauses 12 through 15. 7.16 CR 3.14 – Integrity of the boot process The integrity of the boot proc ess requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15. 8 FR 4 – Data confidentiality 8.1 Purpose and SL-C(DC) descriptions Ensure the confidentiality of information on communication channels and in data stored in repositories to protect against unauthorized disclosure. • SL 1 – Prevent the unauthorized disclosure of information via eavesdropping or casual exposure. • SL 2 – Prevent the unauthorized disclosure of information to an entity actively searching for it using simple means with low resources, generic skills and low motivation. • SL 3 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with extended resources, IACS specific skills and high motivation. | SR3.9.1 | SR 3.9 RE (1) | Audit records on write- once media | The control system shall provide the capability to produce audit records on hardware- enforced write -once media. 7.11.3.2 Void | Audit information includes all information (for example, audit records, audit settings and audit reports) needed to successfully audit control system activity. The audit information is important for error correction, security breach recovery, investigations and related efforts. Mechanisms for enhanced protection against modification and deletion include the storage of audit information to hardware- enforced write- once media. | The requirements for the four SL levels that relate to SR 3.9 – Protection of audit information are: • SL-C(SI, control system) 1: Not selected • SL-C(SI, control system) 2: SR 3.9 • SL-C(SI, control system) 3: SR 3.9 • SL-C(SI, control system) 4: SR 3.9 (1) 8 FR 4 – Data confidentiality 8.1 Purpose and SL-C(DC) descriptions Ensure the confidentiality of information on communication channels and in data repositories to prevent unauthorized disclosure. • SL 1 – Prevent the unauthorized disclosure of information via eavesdropping or casual exposure. • SL 2 – Prevent the unauthorized disclosure of information to an entity actively searching for it using simple means with low resources, generic skills and low motivation. • SL 3 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with extended resources, IACS specific skills and high motivation. 8.2 Rationale Some control system -generated information, whether at rest or in transit, is of a confidential or sensitive na ture. This implies that some communication channels and data- stores require protection against eavesdr opping and unauthorized access. | Same base identifier and enhancement sequence
52 | 4 | Base requirement | CR4.1 | CR 4.1 | CR | Information confidentiality | Component s shall a) provide the capability to protect the confidentiality of information at rest for which explicit read authorization is supported; and © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 b) support the protect ion of the confidentiality of information in transit as defined in IEC 62443‑3‑3 SR 4.1. | The decision whether a given information should be protected or not depends on the context and cannot be made at product design. However, the fact that an organization limits access to information by configuring explicit read authorizations in the control system is an indicator that this information should be protected by the organization. Thus, all information for which the component supports the capability to assign explicit read authorizations should be considered potentially sensitive and thus the component should also provide the capability to protect its confi dentiality. Confidentiality of information in transit requir es system level capabilities which the component should be able to support. For confidentiality protection, 8.5 provides further requirements. | The requirements for the four SL levels that relate to CR 4.1 are: • SL-C(DC, component) 1: CR 4.1 • SL-C(DC, component) 2: CR 4.1 • SL-C(DC, component) 3: CR 4.1 • SL-C(DC, component) 4: CR 4.1 | SR4.1 | SR 4.1 | Information confidentiality | The control system shall provide the capability to protect the confidentiality of information for which explicit read authorization is suppor ted, whether at rest or in transit. | Protection of information, at rest or in transit, can be maintained through physical means, compartmentalization or encry ption, among other techniques. It is crucial that the technique chosen consider s the potential ramifications on control system performance and the capability to recover from system failure or attack. The decision whether the confidentiality of a given piece of information should be protected or not depends on the context and cannot be made at product design. However, the fact that an organization limits access to information by configuring explicit read authorizations in the control system is an indicator that this information is considered confidential by the organization. Thus, all information for which the control system supports the capability to assign explicit read authorizations should be considered potentially confidential and thus the control system should also provide the capability to prot ect it. Different organizations and industries may require different levels of encryption strength for different categories of information, based on the sensitivity of the information as well as industry standards and regulatory requirements (see 8.5, SR 4.3 – Use of cryptography). In some situations network configuration information stored and processed in switches and routers may be considered as confidential. Communications involving exposed information transfer may be vulnerable to eavesdropping or tampering. If the control system is depending upon an external commu nications service provider, it may be more difficult to obtain the necessary assurances regarding the implementation of needed security requirements for communication confidentiality. In such cases, it may be appropriate to implement compensating countermeasures or explicitly accept the additional risk. Entities should also be cognizant of information confidentiality when portable and mobile devices are utilized (for example, engineering laptops and USB sticks). As required by 5.7, SR 1.5 – Authenticator management, authentication information, such as passwords, should be considered confidential, and thus never be sent in the clear. | The requirements for the four SL levels that relate to SR 4.1 – Information confidentiality are: • SL-C(DC, control system) 1: SR 4. 1 • SL-C(DC, control system) 2: SR 4. 1 (1) • SL-C(DC, control system) 3: SR 4. 1 (1) • SL-C(DC, control system) 4: SR 4. 1 (1) (2) | Same base identifier and enhancement sequence
53 | 4 | Base requirement | CR4.2 | CR 4.2 | CR | Information persistence | Component s shall provide the capability to erase all information, for which explicit read authorization is supported, from components to be released from active service and/or decommissioned. | Removal of a control system component from active service should not provide the opportunity for unintentional release of information for which explicit read authorization is supported. An example of such information can include authentication information and network configuration information stored in non -volatile storage or other cryptographic information that would facilitate unauthorized or malicious activity. Information produced by the actions of a user or role (or the actions of a software process acting on behalf of a user or role) should not be disclosed to a different user or role in an uncontrolled fashion. Control of control system information or data persistence prevents information stored on a shared resource from being unintentionally disclos ed after that resource has been released back to the control system. | The requirements for the four SL levels that relate to CR 4.2 are: • SL-C(DC, component) 1: Not selected • SL-C(DC, component) 2: CR 4.2 • SL-C(DC, component) 3: CR 4.2 (1) (2) • SL-C(DC, component) 4: CR 4.2 (1) (2) | SR4.2 | SR 4.2 | Information persisten ce | The control system shall provide the capability to purge all information for which explicit read authorization is supported from components to be released from active service and/or decommissioned. | Removal of a control system component from active service should not provide the opportunity for unintentional release of information for which explicit read authorization is supported. An example of such information would include ‘join keys’ (in the case of some wireless field devices) stored in non -volatile storage or other cryptographic information that would facilitate unauthorized or malicious activity. Information produced by the actions of a user or role (or the actions of a software process acting on behalf of a user or role) should not be disclosed to a different user or role in an uncontrolled fashion. Control of control system information or data persistence prevents information stored on a shared resource from being unintentionally disclosed after that resource has been released back to the control system. | The requirements for the four SL levels that relate to SR 4.2 – Information persistence are: • SL-C(DC, control system) 1: Not Selected • SL-C(DC, control system) 2: SR 4.2 • SL-C(DC, control system) 3: SR 4.2 (1) • SL-C(DC, control system) 4: SR 4.2 (1) | Same base identifier and enhancement sequence
54 | 4 | Enhancement | CR4.2.1 | CR 4.2 RE (1) | CR | Erase of shared memory resources | Component s shall provide the capability to protect against unauthorized and unintended information transfer via volatile shared memory resources. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 Volatile memory resources are those that generally do not retain information after being released to memory management. However, there are attacks against random access memory (RAM) which might extract key material or other confidential data before it is actually over -written. Therefore, when volatile shared memory is released back to the control system for use by a different user, all unique data and connections to unique data need to be purged from the resource so it is not visible or accessible to the new user. | Removal of a control system component from active service should not provide the opportunity for unintentional release of information for which explicit read authorization is supported. An example of such information can include authentication information and network configuration information stored in non -volatile storage or other cryptographic information that would facilitate unauthorized or malicious activity. Information produced by the actions of a user or role (or the actions of a software process acting on behalf of a user or role) should not be disclosed to a different user or role in an uncontrolled fashion. Control of control system information or data persistence prevents information stored on a shared resource from being unintentionally disclos ed after that resource has been released back to the control system. | The requirements for the four SL levels that relate to CR 4.2 are: • SL-C(DC, component) 1: Not selected • SL-C(DC, component) 2: CR 4.2 • SL-C(DC, component) 3: CR 4.2 (1) (2) • SL-C(DC, component) 4: CR 4.2 (1) (2) | SR4.2.1 | SR 4.2 RE (1) | Purging of shared memory resources | The control system shall provide the capability to prevent unauthorized and unintended information transfer via volatile shared memory resources. NOTE Volatile memory resources are those that typically do not retain information after being released to memory management. However, there are attacks against random access memory (RAM) that have the potential to extract key material or other confidential data before it is actually over -written. Therefore, it is a commonly accepted practice to purge all unique data and connections to unique data from volatile shared memory when that memory is released back to the control system for use by a different user, such that this data is not visible or accessible to the new user. 8.4.3.2 Void | Removal of a control system component from active service should not provide the opportunity for unintentional release of information for which explicit read authorization is supported. An example of such information would include ‘join keys’ (in the case of some wireless field devices) stored in non -volatile storage or other cryptographic information that would facilitate unauthorized or malicious activity. Information produced by the actions of a user or role (or the actions of a software process acting on behalf of a user or role) should not be disclosed to a different user or role in an uncontrolled fashion. Control of control system information or data persistence prevents information stored on a shared resource from being unintentionally disclosed after that resource has been released back to the control system. | The requirements for the four SL levels that relate to SR 4.2 – Information persistence are: • SL-C(DC, control system) 1: Not Selected • SL-C(DC, control system) 2: SR 4.2 • SL-C(DC, control system) 3: SR 4.2 (1) • SL-C(DC, control system) 4: SR 4.2 (1) | Same base identifier and enhancement sequence
55 | 4 | Enhancement | CR4.2.2 | CR 4.2 RE (2) | CR | Erase verification | Component s shall provide the capability to verify that the erasure of information occurred. | Removal of a control system component from active service should not provide the opportunity for unintentional release of information for which explicit read authorization is supported. An example of such information can include authentication information and network configuration information stored in non -volatile storage or other cryptographic information that would facilitate unauthorized or malicious activity. Information produced by the actions of a user or role (or the actions of a software process acting on behalf of a user or role) should not be disclosed to a different user or role in an uncontrolled fashion. Control of control system information or data persistence prevents information stored on a shared resource from being unintentionally disclos ed after that resource has been released back to the control system. | The requirements for the four SL levels that relate to CR 4.2 are: • SL-C(DC, component) 1: Not selected • SL-C(DC, component) 2: CR 4.2 • SL-C(DC, component) 3: CR 4.2 (1) (2) • SL-C(DC, component) 4: CR 4.2 (1) (2) | [6 empty] | No corresponding SR
56 | 4 | Base requirement | CR4.3 | CR 4.3 | CR | Use of cryptography | If cryptography is required, the component shall use cryptographic security mechanisms according to internationally recognized and proven security practices and recommendations. | The selection of cryptographic protection should be based on a threat and risk analysis wh ich covers the value of the information being protected, the consequences of the confidentiality and integrity of the information being breached, the time period during which the information is confidential and control system operating constraints. This can involve either information at rest, in transit, or both. Note that backups are an example of information at rest, and should be considered as part of a data confidentiality and integrity assessment process. The control system product supplier should document the practices and procedures relating to cryptographic key establishment and management. The control system should utilize established and tested encryption and hash algorithms, such as the advanced encryption standard (AES) and the secure hash algorithm (SHA) series, and key sizes based on an assigned standard. Key generation needs to be performed using an effective random number generator. The security policies and procedures for key management need to address periodic key changes, key destruction, key distribution and encryption key backup in accordance with defined standards. Generally accepted practices and recommendations can be found in documents such as NIST SP 800 -57, Recommendation for Key Management – Part 1: General [18]. Implementation requirements can be found for example in FIPS 140 -2, Security Requirements for Cryptographic Modules [17] or ISO/IEC 19790 [9]. This CR, along with 5.10, CR 1.8 – Public key infrastructure certificates, may be applicable when meeting many other requirements defined within this document. | The requirements for the four security levels that relate to CR 4.3 are: • SL-C(DC,component) 1: CR 4.3 • SL-C(DC,component) 2: CR 4.3 © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 • SL-C(DC,component) 3: CR 4.3 • SL-C(DC,component) 4: CR 4.3 9 FR 5 – Restricted data flow 9.1 Purpose and SL-C(RDF) descriptions Segment the control system via zones and conduits to limit the unnecessary flow of data. • SL 1 – Prevent the casual or coincidental circumvention of zone and conduit segmentation. • SL 2 – Prevent the intended circumvention of zone and conduit segmentation by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Prevent the intended circumvention of zone and conduit segmentation by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Prevent the intended circumvention of zone and conduit segmentation by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 9.2 Rationale Using their risk assessment methodology defined in IEC 62443‑3‑2 [5], asset owners should determine necessary information flow restrictions and thus, by extension, determine the configuration of the conduits used to deliver this information. Derived recommendations and guidelines should include mechanisms that range from disconnecting control system networks from business or public networks to using unidirectional gateways, single stateful fi rewalls or DMZ configurations to manage the flow of information. | SR4.3 | SR 4.3 | Use of cryptography | If cryptogr aphy is required, the control system shall use cryptographic algorithms, key sizes and mechanisms for key establishment and management according to commonly accepted security industry practices and recommendations. | The selection of cryptographic protection should match the value of the information being protected, the consequences of the confidentiality of the information being breached, the time period during which the information is confidential and control system operating constraints. This can involve either information at rest, in transit, or both. Note that backups are an example of information at rest, and should be considered as part of a data confidentiality assessment process. The control system product supp lier should document the practices and procedures relating to cryptographic key establishment and management. The control system should utilize established and tested encryption and hash algorithm s, such as the advanced encryption standard (AES) and the secure hash algorithm (SHA) series, and key sizes based on an assigned standard. Key generation needs to be performed using an effective random number generator. The security policies and procedures for key management need to address period ic key changes, ke y destruction, key distribution and encryption key backup in accordance with defined standards. Generally accepted practices and recommendations can be found in documents such as NIST SP800- 57 [25]. Implementation requirements can be found for example in ISO/IEC 19790 [12]. This SR, along with 5.10, SR 1.8 – Public key infrastructure (PKI) certificates may be applicable when meeting many other requirements defined within this standard. | The requirements for the four SL levels that relate to SR 4.3 – Use of cryptography are: • SL-C(DC, control system) 1: SR 4.3 • SL-C(DC, control system) 2: SR 4.3 • SL-C(DC, control system) 3: SR 4.3 • SL-C(DC, control system) 4: SR 4.3 9 FR 5 – Restrict ed data flow 9.1 Purpose and SL-C(RDF) descriptions Segment the control system via zones and conduits to limi t the unnecessary flow of data. • SL 1 – Prevent the casual or coincidental circumvention of zone and conduit segmentation. • SL 2 – Prevent the intended circumvention of zone and conduit segmentation by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Prevent the intended circumvention of zone and conduit segmentation by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Prevent the intended circumvention of zone and conduit segmentation by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 9.2 Rationale Using their risk assessment methodology, asset owners need to determine necessary information flow restrictions and thus, by extension, determine the configuration of the condui ts used to deliver this information. Derived prescriptive recommendations and guidelines should include mechanisms that range from disconnecting control system networks from business or public networks to using unidirectional gateways, stateful firewalls and DMZs to manage the flow of information. | Same base identifier and enhancement sequence
57 | 5 | Base requirement | CR5.1 | CR 5.1 | CR | Network segmentation | Component s shall support a segmented network to support zones and conduits, as needed, to support the broader network architecture based on logical segment ation and criticality. | Netwo rk segmentation is used by organizations for a variety of purposes, including cyber security. The main reasons for segmenting networks are to reduce the exposure, or ingress, of network traffic into a control system and reduce the spread, or egress, of net work traffic from a control system. This improves overall system response and reliability as well as provides a measure of cyber security protection. It also allows different network segments within the control system, including critical control systems and safety -related systems, to be segmented from other systems for an additional level of protection. Access from the control system to the World Wide Web should be clearly justified based on control system operational requirements. Network segmentation and the level of protection it provides will vary greatly depending on the overall network architecture used by an asset owner in their facility and even system integrators within their control systems. Logically segmenting networks based on their functionality provides some measure of protection, but may still lead to single- points -of-failure if a network device is compromised. Physically segmenting networks provides another level of protection by removing that single- point -of-failure case, but will lead to a more complex and more costly network design. These trade -offs will need to be evaluated during the network design process (see IEC 62443 ‑2‑1 [1]). © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 In response to an incident, it may be necessary to break the connections between different network segments. In that event, the services necessary to support essential operations should be maintained in such a way that the devices can continue to operate properly and/or shutdown in an orderly manner. This may require that some servers may need to be duplicated on the control system network to support normal network features, for example dynamic host configuration protocol (DHCP), domain name servi ce (DNS) or local CAs. It may also mean that some critical control systems and safety -related systems be designed from the beginning to be completely isolated from other networks. | The requirements for the four SL levels that relate to CR 5.1 are: • SL-C(RDF, component) 1: CR 5.1 • SL-C(RDF, component) 2: CR 5.1 • SL-C(RDF, component) 3: CR 5.1 • SL-C(RDF, component) 4: CR 5.1 9.4 CR 5.2 – Zone boundary protection The zone boundary protection requirements are network -component -specific and can be located as requirements for network devices in Clause 15. 9.5 CR 5.3 – General -purpose person -to-person communication restrictions The general -purpose person- to-person communication restriction requirements are network - component -specific and can be located as requirements for network devices in Clause 15. 9.6 CR 5.4 – Application partitioning There is no component level requirement associated with IEC 62443‑3‑3 SR 5.4. 10 FR 6 – Timely response to events 10.1 Purpose and SL-C(TRE) descriptions Respond to security violations by notifying the proper authorities, reporting needed evidence of the violation and taking timely corrective action when incidents are discovered. • SL 1 – Monitor the operation of the components of the IACS, and respond to incidents when discovered, by collecting and providing the forensic evidence when queried. • SL 2 – Monitor the operation of the components of the IACS, and respond to incidents when discovered, by actively collecting and periodically reporting forensic evidence. • SL 3 – Monitor the operation of the components of the IACS, and respond to incidents when discovered, by actively collecting and pushing forensic evidence to the proper authorities. • SL 4 – Monitor the operation of the components of the IACS, and respond to incidents when discovered, by actively collecting and pushing forensic evidence to the proper authorities in near real -time. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 10.2 Rationale Although a system may begin operation in a secure state, it is important to be able to monitor the system to ensure that it remains in that secure state. If an event impacts the security of a system, timely notification of the event may be critical to mitigating the associated risk. Asset owners should establish security policies and procedures and proper lin es of communication and control needed to respond to security violations. Derived recommendations and guidelines should include mechanisms that collect, report, preserve and automatically correlate the forensic evidence to ensure timely corrective action. The use of monitoring tools and techniques should not adversely affect the operational performance of the control system. | SR5.1 | SR 5.1 | Network segmentation | The control system shall provide the capability to logically segment control system networks from non- control system networks and to lo gically segment critical control system networks from other control system networks. | Network segmentation is used by organizations for a variety of purposes, including cyber security. The main reasons for segmenting networks are to reduce the exposure, or ingress, of network traffic into a control system and reduce the spread, or egress, of network traffic from a control system. This improves overall system response and reliability as well as provides a measure of cyber security protection. It also allows different network segments within the control system, including critical control systems and safety -related systems, to be segmented from other systems for an additional level of protection. Access from the control system to the World Wide Web should be clearly justified based on control system operational requirements. Network segmentation and the level of protection it provides will vary greatly d epending on the overall network architecture used by an asset owner in their facility and even system integrators within their control systems. Logically segmenting networks based on their functionality provides some measure of protection, but may still lead to single- points -of-failure if a network device is compromised. Physically segmenting networks provides another level of protection by removing that single- point -of-failure case, but will lead to a more complex and costly network design. These trade- offs will need to be evaluated during the network design process (see IEC 62443‑2‑1). In response to an incident, it may be necessary to break the connections between different network segments. In that event, the services necessary to support essential operations should be maintained in such a way that the devices can continue to operate properly and/or shutdown in an orderly manner. This may require that some servers may need to be duplicated on the control system network to support normal network features, for example dynamic host configuration protocol (DHCP), domain name service (DNS) or local CAs. It may also mean that some critical control systems and safety -related systems be designed from the beginning to be completely isolated from other networks. | The requirements for the four SL levels that relate to SR 5. 1 – Network segmentation are: • SL-C(RDF, control system) 1: SR 5. 1 • SL-C(RDF, control system) 2: SR 5. 1 (1) • SL-C(RDF, control system) 3: SR 5. 1 (1) (2) • SL-C(RDF, control system) 4: SR 5. 1 (1) (2) (3) | Same base identifier and enhancement sequence
58 | 6 | Base requirement | CR6.1 | CR 6.1 | CR | Audit log accessibility | Component s shall provide the capability for authorized humans and/or tools to access audi t logs on a read -only basis. | The applications and devices may generate audit recor ds about events occurring in that application or device (see 6.10). Access to these audit logs is necessary to support filtering audit logs, identifying and removing information that is redundant, reviewing and reporting activity during after -the-fact investigations of security incidents. In general, audit reduction and report generation should be performed on a separate information system. Manual access to the audit records (such as, screen views or printouts) is sufficient for meeting t he base requirement, but is insufficient for higher SLs. Programmatic access is commonly used to provide the audit log information to analysis mechanisms such as security information and event management (SIEM). | The requirements for the four SL levels that relate to CR 6.1 are: • SL-C(TRE, component) 1: CR 6.1 • SL-C(TRE, component) 2: CR 6.1 • SL-C(TRE, component) 3: CR 6.1 (1) • SL-C(TRE, component) 4: CR 6.1 (1) | SR6.1 | SR 6.1 | Audit log acc essibility | The control system shall provide the capability for authorized humans and/or tools to access audit logs on a read -only basis. | The control system generates audit records about events occurring in the system (see 6.10, SR 2.8 – Auditable events). Access to these audit log s is necessary to support filtering audit logs, identifying and removing information that is redundant, review ing and reporting activity during after -the-fact investigations of security incidents. This access should not alter the original audit records. In general, audit reduction and report generation should be performed on a separate information system. Manual access to the audit records (such as screen views or printouts) is sufficient for meeting the base requirement, but is insufficient for higher SLs. Programmatic access is commonly used to provide the audit log information to analysis mechanisms such as SIEM. See relevant SRs in Clauses 5, 6 and 9 regarding the creation of, protection of and access to audit logs. | The requirements for the four SL levels that relate to SR 6.1 – Audit log accessibility are: • SL-C(TRE, control system) 1: SR 6.1 • SL-C(TRE, control system) 2: SR 6.1 • SL-C(TRE, control system) 3: SR 6.1 (1) • SL-C(TRE, control system) 4: SR 6.1 (1) | Same base identifier and enhancement sequence
59 | 6 | Enhancement | CR6.1.1 | CR 6.1 RE (1) | CR | Programmatic access t o audit logs | Component s shall provide programmatic access to audit records by either using an application programming interface (API) or sending the audit records to a centralized system. | The applications and devices may generate audit recor ds about events occurring in that application or device (see 6.10). Access to these audit logs is necessary to support filtering audit logs, identifying and removing information that is redundant, reviewing and reporting activity during after -the-fact investigations of security incidents. In general, audit reduction and report generation should be performed on a separate information system. Manual access to the audit records (such as, screen views or printouts) is sufficient for meeting t he base requirement, but is insufficient for higher SLs. Programmatic access is commonly used to provide the audit log information to analysis mechanisms such as security information and event management (SIEM). | The requirements for the four SL levels that relate to CR 6.1 are: • SL-C(TRE, component) 1: CR 6.1 • SL-C(TRE, component) 2: CR 6.1 • SL-C(TRE, component) 3: CR 6.1 (1) • SL-C(TRE, component) 4: CR 6.1 (1) | SR6.1.1 | SR 6.1 RE (1) | Programmatic access to audit logs | The control system shall provide programmatic access to audit records using an application programming interface (API). 10.3.3.2 Void | The control system generates audit records about events occurring in the system (see 6.10, SR 2.8 – Auditable events). Access to these audit log s is necessary to support filtering audit logs, identifying and removing information that is redundant, review ing and reporting activity during after -the-fact investigations of security incidents. This access should not alter the original audit records. In general, audit reduction and report generation should be performed on a separate information system. Manual access to the audit records (such as screen views or printouts) is sufficient for meeting the base requirement, but is insufficient for higher SLs. Programmatic access is commonly used to provide the audit log information to analysis mechanisms such as SIEM. See relevant SRs in Clauses 5, 6 and 9 regarding the creation of, protection of and access to audit logs. | The requirements for the four SL levels that relate to SR 6.1 – Audit log accessibility are: • SL-C(TRE, control system) 1: SR 6.1 • SL-C(TRE, control system) 2: SR 6.1 • SL-C(TRE, control system) 3: SR 6.1 (1) • SL-C(TRE, control system) 4: SR 6.1 (1) | Same base identifier and enhancement sequence
60 | 6 | Base requirement | CR6.2 | CR 6.2 | CR | Continuous monitoring | Component s shall provide the capability to be continuously monitored using commonly accepted security industry practices and recommendations to detect, characterize and report security breaches in a timely manner. | Control system monitor ing capability can be achieved through a variety of tools and techniques (for example, IDS, intrusion prevention system (IPS), protection from malicious code mechanisms and network monitoring mechanisms). As attacks become more © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 sophisticated, these monitor ing tools and techniques will need to become more sophisticated as well, including for example behaviour- based IDS/IPS. Monitoring devices should be strategically deployed within the control system (for example, at selected perimeter locations and near server farms supporting critical applications) to collect essential information. Monitoring mechanisms may also be deployed at ad hoc locations within the control system to track specific transactions. Monitoring should include appropriate reporting mechani sms to allow for a timely response to events. To keep the reporting focused and the amount of reported information to a level that can be processed by the recipients, mechanisms such as SIEM are commonly applied to correlate individual events into aggregate reports that establish a larger context in which the raw events occurred. | The requirements for the four SL levels that relate to CR 6.2 are: • SL-C(TRE, component) 1: Not s elected • SL-C(TRE, component) 2: CR 6.2 • SL-C(TRE, component) 3: CR 6.2 • SL-C(TRE, component) 4: CR 6.2 11 FR 7 – Resource availability 11.1 Purpose and SL-C(RA) descriptions Ensure the availability of components against the degradation or denial of essential services. • SL 1 – Ensure that the component operates reliably under normal production conditions and prevents denial -of-service situations caused by the casual or coincidental actions of an entity. • SL 2 – Ensure that the component operates reliably under normal and abnormal production conditions and prevents denial -of-service situations by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Ensure that the component operates reliably under normal, abnormal, and extreme production conditions and prevents denial -of-service situations by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Ensure that the component operates reliably under normal, abnormal, and extreme production conditions and prevents denial -of-service situations by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 11.2 Rationale The aim of this series of CRs is to ensure that the component is resilient against various types of DoS events. This includes the partial or total unavailability of component functionality at various levels. In particular, security incidents in the compone nt should not affect essential functions or other safety -related functions. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR6.2 | SR 6.2 | Continuous monitoring | The control system shall provide the capability to continuously monitor all security mechanism performance using commonly accepted security industry practices and recommendations to detect, characterize and report security breaches in a timely manner. NOTE Response time is a local matter outside the scope of this standard. | Control system monitoring capability can be achieved through a variety of tools and techniques (for exam ple, IDS, IPS, malicious code protection mechanisms and network monitoring mechanisms). As attacks become more sophisticated, these monitoring tools and techniques will need to become more sophisticated as well, including for example behavior - based IDS/IPS. Monitoring devices should be strategically deployed within the control system (for example, at selected perimeter locations and near server farms supporting critical applications) to collect essential inf ormation. Monitoring mechanisms may also be deploy ed at ad hoc locations within the control system t o track specific transactions. Monitoring should include appropriate reporting mechanisms to allow for a timely response to events. To keep the reporting focused and the amount of reported information to a level that can be processed by the recipients, mechanisms such as SIEM are commonly applied to correlate individual events into aggregate reports which establish a larger context in which the raw events occurred. Additionally, these mechanisms can be used to track the effect of security changes to the control system (see 6.10, SR 2.8 – Auditable events). Having forensic tools pre -installed can facilitate incident analysis. | The requirements for the four SL levels that relate to SR 6.2 – Continuous monitoring are: • SL-C(TRE, control system) 1: Not Selected • SL-C(TRE, control system) 2: SR 6.2 • SL-C(TRE, control system) 3: SR 6.2 • SL-C(TRE, control system) 4: SR 6.2 11 FR 7 – Resource avail ability 11.1 Purpose and SL-C(RA) descriptions Ensure the availability of the control system against th e degradation or denial of essential services. • SL 1 – Ensure that the control system operates reliably under normal production conditions and prevents DoS situations caused by the casual or coincidental actions of an entity. • SL 2 – Ensure that the control system operates reliably under normal and abnormal production conditions and prevents DoS situations by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Ensure that the control system operates reliably under normal, abnormal, and extreme production conditions and prevents DoS situations by entities using sophisticated means with moderate resour ces, IACS specific skills and moderate motivation. • SL 4 – Ensure that the control system operates reliably under normal, abnormal, and extreme production conditions and prevents DoS situations by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 11.2 Rationale The aim of this series of SRs is to ensure that the control system is resilient against various types of DoS events. This includes the partial or total unavailability of system functionality at various le vels. In particular, security incidents in the control system should not affect SIS or other safety -related functions. | Same base identifier and enhancement sequence
61 | 7 | Base requirement | CR7.1 | CR 7.1 | CR | Denial of service protection | Component s shall provide the capability to maintain essential functions when operating in a degraded mode as the result of a DoS e vent. | Component s may be subjected to differ ent forms of DoS situations. When these occur, the component should be designed in such a manner that it maintains essential functions necessary for continued safe operations while in a degraded mode. | The requirements for the four SL levels that relate to CR 7.1 are: • SL-C(RA, component) 1: CR 7.1 • SL-C(RA, component) 2: CR 7.1 (1) • SL-C(RA, component) 3: CR 7.1 (1) • SL-C(RA, component) 4: CR 7.1 (1) | SR7.1 | SR 7.1 | Denial of service protection | The control system shall provide the capability to operate in a degraded mode during a DoS event. | A variety of technologies exist to limit, or in some cases, eliminate the effects of DoS situations. For example, boundary protection devices can filter certain types of packets to protect devices on an intern al, trusted network from being directly affected by DoS events or restricting the information flow to be unidirectional outbound. Specifically, as noted in Clause 4, a DoS event on the control system should not adversely impact any safety -related systems. | The requirements for the four SL levels that relate to SR 7.1 – Denial of service protection are: • SL-C(RA, control system) 1: SR 7.1 • SL-C(RA, control system) 2: SR 7.1 (1) • SL-C(RA, control system) 3: SR 7.1 (1) (2) • SL-C(RA, control system) 4: SR 7.1 (1) (2) | Same base identifier and enhancement sequence
62 | 7 | Enhancement | CR7.1.1 | CR 7.1 RE (1) | CR | Manage communication load from component | Component s shall provide t he capability to mitigate the effects of information and/or message flooding types of DoS events. | Component s may be subjected to differ ent forms of DoS situations. When these occur, the component should be designed in such a manner that it maintains essential functions necessary for continued safe operations while in a degraded mode. | The requirements for the four SL levels that relate to CR 7.1 are: • SL-C(RA, component) 1: CR 7.1 • SL-C(RA, component) 2: CR 7.1 (1) • SL-C(RA, component) 3: CR 7.1 (1) • SL-C(RA, component) 4: CR 7.1 (1) | SR7.1.1 | SR 7.1 RE (1) | Manage communication loads | The control system shall provide the capability to manage communication loads (such as using rate limiting) to mitigate the effects of information flooding types of DoS events. | A variety of technologies exist to limit, or in some cases, eliminate the effects of DoS situations. For example, boundary protection devices can filter certain types of packets to protect devices on an intern al, trusted network from being directly affected by DoS events or restricting the information flow to be unidirectional outbound. Specifically, as noted in Clause 4, a DoS event on the control system should not adversely impact any safety -related systems. | The requirements for the four SL levels that relate to SR 7.1 – Denial of service protection are: • SL-C(RA, control system) 1: SR 7.1 • SL-C(RA, control system) 2: SR 7.1 (1) • SL-C(RA, control system) 3: SR 7.1 (1) (2) • SL-C(RA, control system) 4: SR 7.1 (1) (2) | Same base identifier and enhancement sequence
63 | 7 | Base requirement | CR7.2 | CR 7.2 | CR | Resource management | Component s shall provide the capability to limit the use of resources by security functions to protect against resource exhaustion. | Resource management (for example, network segmentation or priority schemes) prevents a lower -priority software process from delaying or interfering with the control system servicing any higher -priority software process. For example, initiating network scans, patching and/or antivirus checks on an operating system can cause severe disruption to normal operations. Traffic rate limiting schemes should be considered as a mitigation technique. | The requirements for the four SL levels that relate to CR 7.2 are: • SL-C(RA, component) 1: CR 7.2 • SL-C(RA, component) 2: CR 7.2 • SL-C(RA, component) 3: CR 7.2 • SL-C(RA, component) 4: CR 7.2 © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR7.2 | SR 7.2 | Resource m anagement | The control system shall provide the capability to limit the use of resources by security functions to prevent resource exhaustion. | Resource management (for example, network segmentation or priority schemes) prevent s a lower -priority software process from delaying or interfering with the control system servicing any higher -priority software process. For example, initiating network scans, patching and/or antivirus checks on an operating system can cause severe disruption to normal operations. Traffic rate limiting schemes should be considered as a mitiga tion technique. | The requirements for the four SL levels that relate to SR 7.2 – Resource management are: • SL-C(RA, contr ol system) 1: SR 7.2 • SL-C(RA, control system) 2: SR 7.2 • SL-C(RA, control system) 3: SR 7.2 • SL-C(RA, control system) 4: SR 7.2 | Same base identifier and enhancement sequence
64 | 7 | Base requirement | CR7.3 | CR 7.3 | CR | Control system backup | Component s shall provide the capability to participate in system level backup operations in order to safeguard the component state (user - and system -level information). The backup process shall not affect the normal component operations. | The availability of up- to-date backups is essential for recovery from a control system failure and/or misconfiguration. Automating this function ensures that all required files are captured, reducing operator overhead. When designing to support a backup capability, consideration should be given to information that will be stored in backups. Some of this inform ation may contain cryptographic keys and other information that is protected through security controls while part of the system. Once the information is placed into a backup it most likely will not have the same controls in place to protect it. Thus, the c omponent backup ability needs to include the mechanisms to support the necessary protection of the information that is contained in the backup. This may include encryption of the backup, encryption of the sensitive data as part of the backup procedure or not including the sensitive information as part of the backup. If the backup is encrypted it is important not to include the cryptographic keys as part of the backup but to backup the cryptographic keys as part of a separate more secure backup procedure. | The requirements for the four SL l evels that relate to CR 7.3 are: • SL-C(RA, component) 1: CR 7.3 • SL-C(RA, component) 2: CR 7.3 (1) • SL-C(RA, component) 3: CR 7.3 (1) • SL-C(RA, component) 4: CR 7.3 (1) | SR7.3 | SR 7.3 | Control system backup | The identity and location of critical files and the ability to conduct backups of user -level and system -level information (including system state information) shall be supported by the control system without affe cting normal plant operations. | The a vailability of up -to-date backups is essential for recovery from a control system failure and/or mis-configuration. Automating this function ensures that all required files are captured, reducing operator overhead. Although not usually requir ed for control system recovery, information required for post -incident forensic activity (for example, audit logs) should be specifically included in the backup (see 10.4, SR 6.2 – Continuous monitoring). If the resulting backups contain confidential information, encryption should be considered (see 8.5, SR 4.3 – Use of cryptography). | The requirements for the four SL levels that relate to SR 7.3 – Control system backup are: • SL-C(RA, control system) 1: SR 7.3 • SL-C(RA, control system) 2: SR 7.3 (1) • SL-C(RA, control system) 3: SR 7.3 (1) (2) • SL-C(RA, control system) 4: SR 7.3 (1) (2) | Same base identifier and enhancement sequence
65 | 7 | Enhancement | CR7.3.1 | CR 7.3 RE (1) | CR | Backup integrity verification | Component s shall provide the capability to validate the integrity of backed up information prior to the initiation of a restore of that information. | The availability of up- to-date backups is essential for recovery from a control system failure and/or misconfiguration. Automating this function ensures that all required files are captured, reducing operator overhead. When designing to support a backup capability, consideration should be given to information that will be stored in backups. Some of this inform ation may contain cryptographic keys and other information that is protected through security controls while part of the system. Once the information is placed into a backup it most likely will not have the same controls in place to protect it. Thus, the c omponent backup ability needs to include the mechanisms to support the necessary protection of the information that is contained in the backup. This may include encryption of the backup, encryption of the sensitive data as part of the backup procedure or not including the sensitive information as part of the backup. If the backup is encrypted it is important not to include the cryptographic keys as part of the backup but to backup the cryptographic keys as part of a separate more secure backup procedure. | The requirements for the four SL l evels that relate to CR 7.3 are: • SL-C(RA, component) 1: CR 7.3 • SL-C(RA, component) 2: CR 7.3 (1) • SL-C(RA, component) 3: CR 7.3 (1) • SL-C(RA, component) 4: CR 7.3 (1) | SR7.3.1 | SR 7.3 RE (1) | Backup verification | The control system shall provide the capability to verify the reliability of backup mechanisms. | The a vailability of up -to-date backups is essential for recovery from a control system failure and/or mis-configuration. Automating this function ensures that all required files are captured, reducing operator overhead. Although not usually requir ed for control system recovery, information required for post -incident forensic activity (for example, audit logs) should be specifically included in the backup (see 10.4, SR 6.2 – Continuous monitoring). If the resulting backups contain confidential information, encryption should be considered (see 8.5, SR 4.3 – Use of cryptography). | The requirements for the four SL levels that relate to SR 7.3 – Control system backup are: • SL-C(RA, control system) 1: SR 7.3 • SL-C(RA, control system) 2: SR 7.3 (1) • SL-C(RA, control system) 3: SR 7.3 (1) (2) • SL-C(RA, control system) 4: SR 7.3 (1) (2) | Same base identifier and enhancement sequence
66 | 7 | Base requirement | CR7.4 | CR 7.4 | CR | Control system recovery and reconstitution | Component s shall provide the capability to be recover ed and reconstitute d to a known secure state after a disruption or failure. | Component recovery and reconstitution to a known secure state means that all system parameters (either default or configurable) are set to secure values, security -critical patches are reinstalled, security -related configuration settings are reestablished, system documentation and operating procedures are available, components are reinstalled and configured with established settings, information from the most recent, known secure backups is loaded and the system is fully tested and functional. | The requirements for the four SL levels that relate to CR 7.4 are: • SL-C(RA, component) 1: CR 7.4 • SL-C(RA, component) 2: CR 7.4 • SL-C(RA, component) 3: CR 7.4 • SL-C(RA, component) 4: CR 7.4 | SR7.4 | SR 7.4 | Control system recovery and reconstitution | The control system shall provide the capability to recover and reconstitut e to a known secure state afte r a disruption or failure. | Control system recovery and reconstitution to a known secure state means that all system parameters (either default or configurable) are set to secure values, security -critical patches are reinstalled, security -related configuration settings are reestablished, system documentation and operating procedures are available, application and system software is reinstalled and configured with secure settings, information from the most recent, known secure backups is loaded and the system is fully tested and functional. | The requirements for the four SL levels that relate to SR 7.4 – Control system recovery and reconstitution are: • SL-C(RA, control system) 1: SR 7.4 • SL-C(RA, control system) 2: SR 7.4 • SL-C(RA, control system) 3: SR 7.4 • SL-C(RA, control system) 4: SR 7.4 | Same base identifier and enhancement sequence
67 | 7 | Base requirement | CR7.6 | CR 7.6 | CR | Network and security configuration settings | Component s shall provide the capability to be configured according to recommended network and security configurations as described in guidelines provided by the control system supplier. The component shall provide an interface to the currently deployed network and security configuration settings. | These configuration settings are the adjustable parameters of the control system components. By default, the component should be configured to the recommended settings. In order for a component to detect and correct any deviations from the approved and/or recommended configuration settings, the component needs to support monitoring and control of changes to the configuration settings in accordance with security policies and procedures. | The requirements for the four SL levels that relate to CR 7.6 are: • SL-C(RA, component) 1: CR 7.6 • SL-C(RA, component) 2: CR 7.6 • SL-C(RA, component) 3: CR 7.6 (1) • SL-C(RA, component) 4: CR 7.6 (1) | SR7.6 | SR 7.6 | Network and security configuration settings | The control system shall provide the capability to be configured according to recommended network and security configurations as described in guidelines provided by the control system supplier. The control system shall provide an interface to the currently deployed network and security configuration settings. | These configuration settings are the adjustable parameters of the control system components. In order to be able to detect and correct any deviations from the approved and/or recommended configuration settings, the control system needs to support monitoring and control of changes to the configuration settings in accordance with security policies and procedures. For enhanced security, an automated check may be performed where the current settings are automatically collected by an agent and compared to approved settings. | The requirements for the four SL levels that relate to SR 7.6 – Network and security configuration settings are: • SL-C(RA, control system) 1: SR 7.6 • SL-C(RA, control system) 2: SR 7.6 • SL-C(RA, control system) 3: SR 7.6 (1) • SL-C(RA, control system) 4: SR 7.6 (1) | Same base identifier and enhancement sequence
68 | 7 | Enhancement | CR7.6.1 | CR 7.6 RE (1) | CR | Machine- readable reporting of current security settings | Component s shall provide the capability to generate a report listing the currently deployed security settings in a machine- readable format. | These configuration settings are the adjustable parameters of the control system components. By default, the component should be configured to the recommended settings. In order for a component to detect and correct any deviations from the approved and/or recommended configuration settings, the component needs to support monitoring and control of changes to the configuration settings in accordance with security policies and procedures. | The requirements for the four SL levels that relate to CR 7.6 are: • SL-C(RA, component) 1: CR 7.6 • SL-C(RA, component) 2: CR 7.6 • SL-C(RA, component) 3: CR 7.6 (1) • SL-C(RA, component) 4: CR 7.6 (1) | SR7.6.1 | SR 7.6 RE (1) | Machine- readable reporting of current security settings | The control system shall provide the capability to generate a report listing the currently deployed security settings in a machine -readable format. 11.8.3.2 Void | These configuration settings are the adjustable parameters of the control system components. In order to be able to detect and correct any deviations from the approved and/or recommended configuration settings, the control system needs to support monitoring and control of changes to the configuration settings in accordance with security policies and procedures. For enhanced security, an automated check may be performed where the current settings are automatically collected by an agent and compared to approved settings. | The requirements for the four SL levels that relate to SR 7.6 – Network and security configuration settings are: • SL-C(RA, control system) 1: SR 7.6 • SL-C(RA, control system) 2: SR 7.6 • SL-C(RA, control system) 3: SR 7.6 (1) • SL-C(RA, control system) 4: SR 7.6 (1) | Same base identifier and enhancement sequence
69 | 7 | Base requirement | CR7.7 | CR 7.7 | CR | Least functionality | Component s shall provide the capability to specifically restrict the use of unnecessary functions, ports, protocols and/or services. | Components are capable of providing a wide variety of functions and services. Some of the functions and services provided may not be necessary to support IACS functionality. Therefore, by default, functions beyond a baseline configuration should be disabled. Additionally, it is sometimes convenient to provide multiple services from a single component © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 of a control system, but doing so increases the risk compared to limiting the services provided by any one component. | The requirements for the four SL levels that relate to CR 7.7 are: • SL-C(RA, component) 1: CR 7.7 • SL-C (RA, component) 2: CR 7.7 • SL-C(RA, component) 3: CR 7.7 • SL-C(RA, component) 4: CR 7.7 | SR7.7 | SR 7.7 | Least functionality | The control system shall provide the capability to specifically prohibit and/or restrict the use of unnecessary functions, ports, protocols and/or services. | Control systems are capable of providing a wide var iety of functions and services. Some of the functions and services provided may not be necessary to support essential func tions. Therefore, by default, functions beyond a baseline configuration should be disabled. Additionally, it is sometimes convenient t o provide multiple services from a single component of a control system, but doing so increases risk over limiting the services provided by any one component. Many functions and services commonly provided by commercial -off-the-shelf (COTS) equipment may be candidates for elimination, for example, email, voice over internet protocol (VoIP), instant messaging (IM), file transfer protocol (FTP), hypertext transfer protocol (HTTP) and file sharing. | The requirements for the four SL levels that relate to SR 7.7 – Least functionality are: • SL-C(RA, control system) 1: SR 7.7 • SL-C(RA, control system) 2: SR 7.7 • SL-C(RA, control system) 3: SR 7.7 • SL-C(RA, control system) 4: SR 7.7 | Same base identifier and enhancement sequence
70 | 7 | Base requirement | CR7.8 | CR 7.8 | CR | Control system component inventory | Component s shall provide the capability to support a control system component inventory according to IEC 62443 -3-3 SR 7.8. | Components may bring their own set of components into the overall control system. When this is the case then thos e components need to provide a mechanism to augment the overall component inventory which is compatible with IEC 62443 ‑2‑4 [3] SP.06.02. | The requirements for the four SL levels that relate to CR 7.8 are: • SL-C(RA, component) 1: Not s elected • SL-C(RA, component) 2: CR 7.8 • SL-C(RA, component) 3: CR 7.8 • SL-C(RA, component) 4: CR 7.8 12 Software application requirements 12.1 Purpose The purpose of this set of requirements is to document requirements that are specific to software applications. | SR7.8 | SR 7.8 | Control system component inventory | The control system shall provide the cap ability to report the current list of installed components and their associated properties. | A control system component inventory may include but is not limited to component ID, capability and revision level. The component inventory should be consistent with the SuC. A formal process of configuration management should be deployed to keep control of the changes in the component inventory baseline (see IEC 62443‑2‑1). | The requirements for the four SL levels that relate to SR 7.8 – Control system component inventory are: • SL-C(RA, control system) 1: Not Selected • SL-C(RA, control system) 2: SR 7.8 • SL-C(RA, control system) 3: SR 7.8 • SL-C(RA, control system) 4: SR 7.8 Annex A (informative) Discussion of the SL vector NOTE 1 This annex is based on the paper titled “ Security Assurance Levels: A Vector Approach to Describing Security Requirements ” [28]. The content in this annex has been modified from that original paper to respond to changes in the IEC 62443 series and comments received from reviewers. NOTE 2 The ulti mate home for the majority of the material contained in this annex will be IEC 62443‑1‑1 and IEC 62443‑ 3‑2. At the time of this documents publication, these other documents were being written and/or revised and did not contain the material on the SL vector. This annex has been provided to aid the reader in understanding the SL vector concept. The material in this annex is informative and will be superseded by any normative content included in those other standards. A.1 Overview Safety systems have used the concept of safety integrity levels (SILs) for almost two decades. This allows the safety integrity capability of a component or the safety integrity level of a deployed system to be represented by a single number that defines a protection factor required to ensure the health and safety of people or the environment based on the probability of failure of that component or system. The process to determine the required prot ection factor for a safety system, while complex, is manageable since the probability of a component or system failure due to random hardware failures can be measured in quantitative terms. The overall risk can be calculated based on the consequences that those failures could potentially have on HSE. Security systems have much broader application, a much broader set of consequences and a much broader set of possible circumstances leading up to a possible event. Security systems are still meant to protect HS E, but they are also meant to protect the industrial process itself, company -proprietary information, public confidence and national security among other things in situations where random hardware failures may not be the root cause. In some cases, it may b e a well -meaning employee that makes a mistake, and in other cases it may be a devious attacker bent on causing an event and hiding the evidence. The increased complexity of security systems makes compressing the protection factor down to a single number m uch more difficult. A.2 Security levels A.2.1 Definition The following is an excerpt from 5.11.1 of IEC/TS 62443‑1‑1:2009 that provides a good explanation of what SLs are and how they can be used. Security levels provide a qualitative approach to addressing security for a zone. As a qualitative method, security level definition has applicability for comparing and managing the security of zones within an organization. As more data becomes available and the mathematical repres entations of risk, threats, and security incidents are developed, this concept will move to a quantitative approach for selection and verification of Security Levels (SL). It will have applicability to both end user companies, and vendors of IACS and security products. It will be used to select IACS devices and countermeasures to be used within a zone and to identify and compare security of zones in different organizations across industry segments. In the first phase of development, the IEC 62443 series of standards tends to use qualitative SLs, using terms such as “low”, “medium”, and “high”. The asset owner will be required to come up with their own definition of what those classifications mean for their particul ar application. The long -term goal for the IEC 62443 series is to move as many of the security levels and requirements to quantita tive descriptions, requirements and metrics as possible to establish repeatable applications of the standard across multiple companies and industries. Achieving this goal will take time, since more experience in applying the standards and data on industrial security systems will need to be acquired to justify the quantitative approach. When mapping requirements to the different SLs, standard developers need some frame of reference describing what the different SLs mean and how they differ from each other. The goal of this annex is to propose such a frame of reference. A.2.2 Types of SLs SLs have been broken down into three different types: target, achieved and capabilit y. These types, while they all are related have to do with different aspects of the security lifecycle. • Target SLs (SL-T) are the desired level of security for a particular system. This is usually determined by performing a risk assessment on a system and determining that it needs a particular level of security to ensure its correct operation. • Achieved SLs (SL-A) are the actual level of security for a particular system. Thes e are measured after a system design is available or when a system is in place. They are used to establish that a security system is meeting the goals that were originally set out in the target SLs. • Capability SLs (SL-C) are the security levels that compon ents or systems can provide when properly configured. These levels state that a particular component or system is capable of meeting the target SLs natively without additional compensating countermeasures when properly configured and integrated. Each of these SLs is intended to be used in differ ent phases of the security lifecycle according the IEC 62443 series. Starting with a target for a particular system, an organization would need to build a design that included the capabilities to achieve the desired result. In other words, the design team would first develop the target SL necessary for a particular system. They would then design the system to meet those targets, usually in an iterative process where after each iteration the achieved SLs of the proposed design are measured and compared to the target SLs. As part of that design process, the designers would select components and systems with the necessary capability SLs to meet the target SL requirements – or wh ere such systems and components are not available, complement the available ones with compensating countermeasures. After the system went into operation, the actual SL would be measured as the achieved SL and compared to the target SL. A.2.3 Using SLs When designing a new system (green field) or revising the security of an existing system (brown field), the first step is to break the system into different zones and define conduits connecting these zones where necessary. Details on how to accomplish this are given in IEC 62443‑3‑2. Once a zone model of the system is established each zone and conduit is assigned a target SL, based on a consequence analysis, which describes the desired security for the respective zone or conduit. During this initial zone and conduit analysis, it is not necessary to have completed a detailed system design. It is sufficient to describe the functionality that should be provided by assets in a zone and the connections between zones in order to meet the security objectives. Figure A. 1 and Figure A. 2 show high -level examples of systems broken down into zones connected by conduits. Figure A. 1 is a graphical representation of a control system for a chlorine truck loading station. The full use- case that accompanies this figure will be discussed in IEC/TR 62443‑1‑4. It has five zones shown: the basic process control system (BPCS), the SIS, the control center, the plant DMZ, and the enterpri se. The BPCS and SIS both use PLCs to operate different aspects of the loading station with the SIS using a special functional safety PLC (FS -PLC) rated for use in safety systems. The two PLCs are connected via a nonroutable serial or Ethernet connection using a boundary protection device. Each of the PLCs is connected to a local switch with an engineering workstation for programming and HMI for operating. The BPCS and SIS zone s also contain an instrument asset management system (IAMS) to measure and test the instruments. A control center containing multiple workstations and the BPCS are both connected to the plant DMZ. A plant DMZ can house a variety of components and systems, for example a data historian and a maintenance workstation as shown in the figure. The plant DMZ is shown connected to the enterprise systems, which contain the corporate wireless local area network (WLAN) and web server. Multiple domain controllers and boundary protection devices are shown in the figure to indicate some of the count ermeasures that may be applied to improve security. Figure A.1 – High -level process- industry example showing zones and conduits Figure A. 2 is a graphical representation of a manufacturing plant. It has four zones defined: the enterprise network, the industrial/enterprise DMZ, and two industrial networks. The enterprise infrastructure has a WLAN and a connection to the Int ernet. Many companies use a DMZ between important parts of their systems to isolate the network traffic. In this particular example, each industrial network operates relatively independent of each other with its own PLC, field devices, and HMI. IEC 2032/13 Figure A.2 – High -level manufacturing example showing zones and conduits After determining the target SLs, the system can be designed (green field) or redesigned (brown field) to try to meet those target SLs. The design process is usually an iterative approach where the system design is checked against the target multiple times throughout the process. Multiple parts of the IEC 62443 series contain guidance on different aspects of the programmatic and technical requirements that go into the design process. IEC 62443‑2‑1 provides guidance on the programmatic aspects of the design process while IEC 62443‑3‑3 (this standard) and IEC 62443‑4‑2 [10] define system -level and component -level technical security requirements and relate them to different capability SLs. During the design process for a system, it is necessary to evaluate the security capabilities of different components and subsystems. Product suppliers will have to provide these as capability SLs for their components or systems by comparing features and capabilities with the requirements defined in the IEC 62443 series for the different capability SLs. These capability SLs can be used to determine whether a given component or system is capable of meeting the target SL for the system. The product supplier or syste m integrator will also have to provide guidance on how t o configure the component or system to meet the claimed SLs. It is likely that in a particular design there will be some components or systems that cannot fully meet the target SL. Where the capability SL of a component or system is lower than the target SL, compensating countermeasures need to be considered to meet the desired target SL. Compensating countermeasures may include changing the design of the component or system to increase its capabilities, choosing another component or system to meet the target SL or adding additional components or systems to meet the target SL. After each iteration in the design process, the system design’s achieved SLs should be reevaluated to see how they compare to th e target SLs for the system. Once the system design is approved and implemented, the system needs to be evaluated to prevent or mitigate deterioration of the system’s security level. It should be evaluated during or after system modifications and on a regu lar schedule. IEC 62443‑2‑1 provides guidance on the steps necessary to operate the security program and how to evaluate its effectiveness. After the achieved SLs have been determined, it will be necessary to evaluate whether the system is still meeting the original target SLs (for example, using the system requirements IEC 20 33/13 from IEC 62443‑3‑3). If the system is not meeting those requirements, there may be multiple reasons including the lack of maintenance of the program or the need to redesign parts of the system. In essence, the control system security capabilities are determined independent from a given use context, but are used in a given context in order to achieve the targ et SL of the respective system architecture, zones and/or conduits (see Figure A. 3). Figure A. 3 – Schematic of correlation of the use of different SL types A.3 SL vector A.3.1 Foundational requirements SLs are based on the seven FRs for security as defined in IEC 62443‑1‑1: 1) Identification and authentication control (IAC), 2) Use control (UC), 3) System integrity (SI), 4) Data confidentiality (DC), 5) Restrict ed data flow (RDF), 6) Timely response to event s (TRE), and 7) Resource availability (RA). IEC 2034/13 Instead of compressing SLs down to a single number, it is possible to use a vector of SLs that uses the seven FRs above instead of a single protection factor. This vector of SLs allows definable separations between SLs for the different FRs using language. This language can be based on the additional consequences associated with security systems or different attacks against the security objectives addressed by the FRs. The language used in the SL definitions can contain practical explanations of how one system is more secure than another without having to relate everything to HSE consequences. A.3.2 Level definitions A.3.2.1 Overview The IEC 62443 series define SLs in terms of five different levels (0, 1, 2, 3 and 4), each with an increasing level of security. The current model for defining SLs depends on protecting an increasingly more complex threat and differs slightly depending on what type of SL it is applied. For SL -C, this means that a particular component or system is capable of being configured by an as set owner or system integrator to protect against an increasingly complex type of threat. For SL- T, this means that the asset owner or system integrator has determined through a risk assessment that they need to protect this particular zone, system or component against this level of threat. For SL- A, this means that the asset owner, system integrator, product supplier and/or any combination of these has configured the zone, system or component to meet the particular security requirements defined for that SL. The language used for each of the SLs uses terms like casual, coincidental, simple, sophisticated and extended. This language is intentionally vague to allow the same basic language to be used for all of the documents in the IEC 62443 series. Each of the individual documents in the series will define the requirements for the SLs that apply to their particular purpose. While the requirements for each of the SLs will be different throughout the IEC 62443 series, there needs to be a general understanding of what each of the SLs should protect against. The following sections will provide some guidance on how to differentiate between the SLs. A.3.2.2 SL 0: No specific requirements or security protection necessary SL 0 has multiple meanings depending on the situation in which it is applied. In defining SL- C it would mean that the component or system fails to meet some of the SL 1 requirements for that particular FR. This would most li kely be for components or systems that would be part of a larger zone where other components or systems would provide compensating countermeasures. In defining SL- T for a particular zone it means that the asset owner has determined that the results of their risk analysis indicate that less than the full SL 1 specific requirements are necessary for that particular FR on that component or system. This would more likely happen for individual components within a system or zone that do not contribute in any way to the FR -specific requirements. In defining SL -A it would mean that the particular zone fails to meet some of the SL 1 requirements for that particular FR. A.3.2.3 SL 1: Protection against casual or coincidental violation Casual or coincidental violations of security are usually through the lax application of security polici es. These can be caused by well -meaning employees just as easily as they can be by an outsider threat. Many of these violations will be security program related and will be handled by enforcing policies and procedures. Using Figure A. 1, a simple example would be an operator able to change a set point on the engineering station in the BPCS zone to a value outside certain conditions determined by the engineering staff. The system did not enforce the proper authentication and use control restrictions to disallow the change by the operator. Also using Figure A. 1, another example would be a password being sent in clear text over the conduit between the BPCS zone and the DMZ zone, allowing a network engineer to view the password while troubleshooting the system. The system did not enforce proper data confidentiality to protect the password. Using Figure A. 2, a third example would be an engineer that means to access the PLC in Industrial Network #1 but actually accesses the PLC in Industrial Network #2. The system did not enforce the proper restriction of data flow preventing the engineer from accessing the wrong system. A.3.2.4 SL 2: Protection against intentional violation using simple means with low resources, generic skills and low motivation Simple means do no t require much knowledge on the part of the attacker. The attacker does not need detailed knowledge of security, the domain or the particular system under attack. These at tack vectors are well known and there may be automated tools for aiding the attacker. They are also designed to attack a wide range of systems instead of targeting a specific system, so an attacker does not need a significant level of motivation or resourc es at hand. Using Figure A. 1, an example would be a virus that infects the maintenance workstation in the Plant DMZ zone spreading to the BPCS engineering workstation since they both use the same general purpose operating system. Using Figure A. 2, another example would be an attacker compromising a web server in the enterprise network by an exploit downloaded from the Internet for a publicly known vulnerability in the general purpose operating system of the web server. The attacker uses the web server as a pivot point in an attack against other systems in the enterprise network as well as the industrial network. Also using Figure A. 2, a third example would be an operator that views a website on the HMI located in Industrial Network #1 which downloads a Trojan t hat opens a hole in the routers and firewalls to the Internet. A.3.2.5 SL 3: Protection against intentional violation using sophisticated means with moderate reso urces, IACS specific skills and moderate motivation Sophisticated means require advanced security knowledge, advanced domain knowledge, advanced knowledge of the target system or any combination of these. An attacker going after a SL 3 system will likely b e using attack vectors that have been customized for the specific target system. The attacker may use exploits in operating systems that are not well known, weaknesses in industrial protocols, specific information about a particular target to violate the security of the system or other means that require a greater motivation as well as skill and knowledge set than are required for SL 1 or 2. An example of sophisticated means could be password or key cracking tools based on hash tables. These tools are avail able for download, but applying them tak es knowledge of the system (such as the hash of a password to crack). Using Figure A. 1, another example would be an attacker t hat gains access to the FS-PLC through the serial conduit after gaining access to the control PLC through a vulnerability in the Ethernet controller. Using Figure A. 2, a third example would be an attacker that gains access to the data historian by using a bruteforce attack through the industrial/enterprise DMZ firewall initiated from the enterprise wireless network. A.3.2.6 SL 4: Protection against intentional violation using sophisticated means with extended resources, IACS specific skills and high motivation SL 3 and SL 4 are very similar in that they both involve sophisticated means used to violate the security requirements of the system. The difference comes from the attacker being even more motivated and having extended resources at their disposal. These may involve high-performance computing resour ces, large numbers of computers or extended periods of time. An example of sophisticated means with extended resources would be using super computers or computer clusters to conduct brute- force password cracking using large hash tables. Another example would be a botnet used to attack a system using multiple attack vectors at once. A third example would be an organized crime organization that has the motivation and resources to spend weeks attempting to analyze a system and develop custom “ zero -day” exploits. A.3.3 SL vector format A vector can be used to describe the security requirements for a zone, conduit, component or system b etter than a single number. This vector may contain either a specific SL requirement or a zero value for each of the foundational requirements (see A.3.1). FORMAT → SL -?([FR,]domain) = { IAC UC SI DC RDF TRE RA } where SL-? = (Required) The SL type (see A.2.2). The possible formats are: • SL-T = Target SL • SL-A = Achieved SL • SL-C = Capabilities SL [FR,] = (Optional) Field indicating the FR that the SL value applies. The FRs are written out in abbreviated form instead of numerical form to aid in readability. domain = (Required) The applicable domain that the SL applies. Domains can refer to zones, control systems, subsystems or components. Some examples of different domains from Figure A. 1 are SIS zone, BPCS zone, BPCS HMI, Plant DMZ domain controller, Plant DMZ to Control Center conduit and SIS to BPCS serial conduit. In this particular standard, all requirements refer to a control system, so the domain term is not used as it would be by ot her documents in the IEC 62443 series. EXAMPLE 1 → SL -T(BPCS Zone) = { 2 2 0 1 3 1 3 } EXAMPLE 2 → SL-C(SIS Engineering Workstation) = { 3 3 2 3 0 0 1 } EXAMPLE 3 → SL-C(RA, FS-PLC) = 4 NOTE The last example specifies only the RA component of a 7- dimension SL-C. Annex B (informative) Map ping of SRs and REs to FR SL levels 1-4 B.1 Overview This annex is intended to provide overall guidance to the reader as to how SL levels 0 to 4 are differentiated on an FR -by-FR basis via the defined SRs and their associated REs. B.2 SL mapping table Table B. 1 indicates which system level requirements apply to which FRs for a given sy stem capability SL – SL-C(xx, control system). For a given FR, the required system level requirements to meet a given SL- C are denoted by a check mark. Thus, as an example, the SL=1 system security capabilities for FR 5 (or SL-C(RDF, control system) =1), would include the base requirements of all four defined SRs. A system unable to meet all four of these SRs would have an SL -C(RDF, control system) =0. To meeting SL-C (RDF, control system) =2, a system needs to support the four SR base requirements plus RE(1) of SR 5. 1 and SR 5. 2. As another example, only the SR 6.1 base requirement is required to meet SL -C(TRE, control system) =1, but both SRs defined are required in order to meet SL-C (TRE, control system) =2. Refer to A.3.3 for how a full SL vector would be denoted. Table B.1 – Mapping of SRs and REs to FR SL levels 1 -4 (1 of 4) SRs and REs SL 1 SL 2 SL 3 SL 4 FR 1 – Identification and authentication control (IAC) SR 1.1 – Human user identification and authentication 5.3     SR 1.1 RE 1 – Unique identification and authentication 5.3.3.1    SR 1.1 RE 2 – Multifactor authentication for untrusted networks 5.3.3.2   SR 1.1 RE 3 – Multifactor authentication for all networks 5.3.3.3  SR 1.2 – Software process and device identification and authentication 5.4    SR 1.2 RE 1 – Unique identification and authentication 5.4.3.1   SR 1.3 – Account management 5.5     SR 1.3 RE 1 – Unified account management 5.5.3.1   SR 1.4 – Identifier management 5.6     SR 1.5 – Authenticator management 5.7     SR 1.5 RE 1 – Hardware security for software process identity credentials 5.7.3.1   SR 1.6 – Wireless access management 5.8     SR 1.6 RE 1 – Unique identification and authentication 5.8.3.1    SR 1.7 – Strength of password -based authentication 5.9     SR 1.7 RE 1 – Password generation and lifetime restrictions for human users 5.9.3.1   Table B. 1 (2 of 4) SRs and REs SL 1 SL 2 SL 3 SL 4 SR 1.7 RE 2 – Password lifetime restrictions for all users 5.9.3.2  SR 1.8 – Public key infrastructure certificates 5.10    SR 1.9 – Strength of public key authentication 5.11    SR 1.9 RE 1 – Hardware security for public key authentication 5.11.3.1   SR 1.10 – Authenticator feedback 5.12     SR 1.11 – Unsuccessful login attempts 5.13     SR 1.12 – System use notification 5.14     SR 1.13 – Access via untrusted networks 5.15     SR 1.13 RE 1 – Explicit access request approval 5.15.3.1    FR 2 – Use control (UC) SR 2.1 – Authorization enforcement 6.3     SR 2.1 RE 1 – Authorization enforcement for all users 6.3.3.1    SR 2.1 RE 2 – Permission mapping to roles 6.3.3.2    SR 2.1 RE 3 – Supervisor override 6.3.3.3   SR 2.1 RE 4 – Dual approval 6.3.3.4  SR 2.2 – Wireless use control 6.4     SR 2.2 RE 1 – Identify and report unauthorized wireless devices 6.4.3.1   SR 2.3 – Use control for portable and mobile devices 6.5     SR 2.3 RE 1 – Enforcement of security status of portable and mobile devices 6.5.3.1   SR 2.4 – Mobile code 6.6     SR 2.4 RE 1 – Mobile code integrity check 6.6.3.1   SR 2.5 – Session lock 6.7     SR 2.6 – Remote session termination 6.8    SR 2.7 – Concurrent session control 6.9   SR 2.8 – Auditable events 6.10     SR 2.8 RE 1 – Centrally managed, system -wide audit trail 6.10.3.1   SR 2.9 – Audit storage capacity 6.11     SR 2.9 RE 1 – Warn when audit record storage capacity threshold reached 6.11.3.1   SR 2.10 – Response to audit processing failures 6.12     SR 2.11 – Timestamps 6.13    SR 2.11 RE 1 – Internal time synchronization 6.13.3.1   SR 2.11 RE 2 – Protection of time source integrity 6.13.3.2  SR 2.12 – Non-repudiation 6.14   SR 2.12 RE 1 – Non-repudiation for all users 6.14.3.1  Table B.1 (3 of 4) SRs and REs SL 1 SL 2 SL 3 SL 4 FR 3 – System integrity (SI) SR 3.1 – Communication integrity 7.3     SR 3.1 RE 1 – Cryptographic integrity protection 7.3.3.1   SR 3.2 – Malicious code protection 7.4     SR 3.2 RE 1 – Malicious code protection on entry and exit points 7.4.3.1    SR 3.2 RE 2 – Central management and reporting for malicious code protection 7.4.3.2   SR 3.3 – Security functionality verification 7.5     SR 3.3 RE 1 – Automated mechanisms for security functionality verification 7.5.3.1   SR 3.3 RE 2 – Security functionality verification during normal operation 7.5.3.2  SR 3.4 – Software and information integrity 7.6    SR 3.4 RE 1 – Automated notification about integrity violations 7.6.3.1   SR 3.5 – Input validation 7.7     SR 3.6 – Deterministic output 7.8     SR 3.7 – Error handling 7.9    SR 3.8 – Session integrity 7.10    SR 3.8 RE 1 – Invalidation of session IDs after session termination 7.10.3.1   SR 3.8 RE 2 – Unique session ID generation 7.10.3.2   SR 3.8 RE 3 – Randomness of session IDs 7.10.3.3  SR 3.9 – Protection of audit information 7.11    SR 3.9 RE 1 – Audit records on write-once media 7.11.3.1  FR 4 – Data confidentiality (DC) SR 4.1 – Information confidentiality 8.3     SR 4.1 RE 1 – Protection of confidentiality at rest or in transit via untrusted networks 8.3.3.1    SR 4.1 RE 2 – Protection of confidentiality across zone boundaries 8.3.3.2  SR 4.2 – Information persistence 8.4    SR 4.2 RE 1 – Purging of shared memory resources 8.4.3.1   SR 4.3 – Use of cryptography 8.5     FR 5 – Restricted data flow (RDF) SR 5.1 – Network segmentation 9.3     SR 5.1 RE 1 – Physical network segmentation 9.3.3.1    SR 5.1 RE 2 – Independence from non-control system networks 9.3.3.2   SR 5.1 RE 3 – Logical and physical isolation of critical networks 9.3.3.3  Table B. 1 (4 of 4) SRs and REs SL 1 SL 2 SL 3 SL 4 SR 5.2 – Zone boundary protection 9.4     SR 5.2 RE 1 – Deny by default, allow by exception 9.4.3.1    SR 5.2 RE 2 – Island mode 9.4.3.2   SR 5.2 RE 3 – Fail close 9.4.3.3   SR 5.3 – General purpose person- to-person communication restrictions 9.5     SR 5.3 RE 1 – Prohibit all general purpose person - to-person communications 9.5.3.1   SR 5.4 – Application partitioning 9.6     FR 6 – Timely response to event s (TRE) SR 6.1 – Audit log accessibility 10.3     SR 6.1 RE 1 – Programmatic access to audit logs 10.3.3.1   SR 6.2 – Continuous monitoring 10.4    FR 7 – Resource availability (RA) SR 7.1 – Denial of service protection 11.3     SR 7.1 RE 1 – Manage communication loads 11.3.3.1    SR 7.1 RE 2 – Limit DoS effects to other systems or networks 11.3.3.2   SR 7.2 – Resource management 11.4     SR 7.3 – Control system backup 11.5     SR 7.3 RE 1 – Backup verification 11.5.3.1    SR 7.3 RE 2 – Backup automation 11.5.3.2   SR 7.4 – Control system recovery and reconstitution 11.6     SR 7.5 – Emergency power 11.7     SR 7.6 – Network and security configuration settings 11.8     SR 7.6 RE 1 – Machine- readable reporting of current security settings 11.8.3.1   SR 7.7 – Least functionality 11.9     SR 7.8 – Control system component inventory 11.10    Bibliography NOTE 1 This bibliography includes references to sources used in the creation of this standard as well as references to sources that may aid the reader in developing a greater understanding of cyber security as a whole and of the process of developing a cyber -security management system. Not all references in this bibliography are referred to throughout the text of this standard. The references have been grouped into different categories based on their source. References to other parts, both existing and in progres s, of the IEC 62443 series: NOTE 2 These references are not all published documents; some of them are in development. They are listed here for completeness of the currently authorized parts of the IEC 62443 series. [1] IEC/TR 62443‑1‑2, Industrial communication networks – Network and system security – Part 1-2: Master glossary of terms and abbreviations 3 [2] IEC/TS 62443‑1‑3, Indust rial communication networks – Network and system security – Part 1-3: System security compliance metrics 4 [3] IEC/TR 62443‑1‑4, Industrial communication networks – Network and system security – Part 1-4: IACS security lifecycle and use- case 5 [4] IEC/TR 62443‑2‑2, Industrial communication networks – Network and system security – Part 2-2: Implementation guidance for an IACS security management system 6 [5] IEC/TR 62443‑2‑3, Industrial communication networks – Network and system security – Part 2-3: Patch management in the IACS environment 7 [6] IEC 62443‑2‑4, Industrial communication networks – Network and system security – Part 2-4: Installation and maintenance requirements for IACS suppliers 8 [7] IEC/TR 62443‑3‑1, Industrial communication networks – Network and system security – Part 3-1: Security technologies for industrial automation and control systems [8] IEC 62443‑3‑2, Industrial communication networks – Network and system security – Part 3-2: Security levels for zones and conduits 9 [9] IEC 62443‑4‑1, Industrial communication networks – Network and system security – Part 4-1: Product development requirements 10 [10] IEC 62443‑4‑2, Industrial communication netwo rks – Network and system security – Part 4-2: Technical security requirements for IACS components 11 ___________ 3 Under consideration. 4 To be published. 5 Under consideration. 6 Under consideration. 7 Under consideration. 8 To be published. 9 Under consideration. 10 Under consideration. 11 Under consideration. Other standards references: [11] ISO/IEC Directives, Part 2:2011, Rules for the structure and drafting of International Standards [12] ISO/IEC 19790, Information techn ology – Security techniques – Security requirements for cryptographic modules [13] ISO/IEC 27002, Information technology – Security techniques – Code of practice for information security management [14] NERC CIP-002, Cyber Secu | Same base identifier and enhancement sequence
71 | 2 | Base requirement | SAR2.4 | SAR 2.4 | SAR | Mobile code | In the event that a software application utilizes mobile code technologies, that application shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the software application: © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 a) Control execution of mobile code; b) Control which users (human, software process, or device) are allowed to transfer mobile code to/from the application; c) Control the executi on of mobile code based on the results of an integrity check prior to the code being executed. | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, portable document format (PDF), Postscri pt, Shockwave movies, Flash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and executed on individual workstations. Control procedures should prevent the develo pment, acquisition or introduction of unacceptable mobile code within the control system in which the component resides. For example, mobile code exchanges may be disallowed directly within the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to SAR 2.4 are: • SL-C(UC, component) 1: SAR 2.4 • SL-C(UC, component) 2: SAR 2.4 (1) • SL-C(UC, component) 3: SAR 2.4 (1) • SL-C(UC, component) 4: SAR 2.4 (1) | SR2.4 | SR 2.4 | Mobile code | The control system shall provide the capability to enforce usage restrictions for mobile code technologies based on the potential t o cause damage to the c ontrol system that includ e: a) preventing the execution of mobile code; b) requiring proper authentication and authorization for origin of the code; c) restricting mobile code transfer to/from the control system; and d) monitoring the use of mobile code. | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, portable document format (PDF), Postscript, Shockwave movies, F lash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and execut ed on individual workstations. Control procedures should preve nt the development, acquisition or introduction of unacceptabl e mobile code within the control system. For example, mobile code exchanges may be disallowed directly with the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to SR 2.4 – Mobile code are: • SL-C(UC, control system) 1: SR 2.4 • SL-C(UC, control system) 2: SR 2. 4 • SL-C(UC, control system) 3: SR 2. 4 (1) • SL-C(UC, control system) 4: SR 2. 4 (1) | Same base identifier and enhancement sequence
72 | 2 | Enhancement | SAR2.4.1 | SAR 2.4 RE (1) | SAR | Mobile code authenticity check | The application shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, portable document format (PDF), Postscri pt, Shockwave movies, Flash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and executed on individual workstations. Control procedures should prevent the develo pment, acquisition or introduction of unacceptable mobile code within the control system in which the component resides. For example, mobile code exchanges may be disallowed directly within the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to SAR 2.4 are: • SL-C(UC, component) 1: SAR 2.4 • SL-C(UC, component) 2: SAR 2.4 (1) • SL-C(UC, component) 3: SAR 2.4 (1) • SL-C(UC, component) 4: SAR 2.4 (1) | SR2.4.1 | SR 2.4 RE (1) | Mobile code integrity check | The control system shall provide the capability to verify integrity of the mobile code before allowing code execution. 6.6.3.2 Void | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, portable document format (PDF), Postscript, Shockwave movies, F lash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and execut ed on individual workstations. Control procedures should preve nt the development, acquisition or introduction of unacceptabl e mobile code within the control system. For example, mobile code exchanges may be disallowed directly with the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to SR 2.4 – Mobile code are: • SL-C(UC, control system) 1: SR 2.4 • SL-C(UC, control system) 2: SR 2. 4 • SL-C(UC, control system) 3: SR 2. 4 (1) • SL-C(UC, control system) 4: SR 2. 4 (1) | Same base identifier and enhancement sequence
73 | 3 | Base requirement | SAR3.2 | SAR 3.2 | SAR | Protection from malicious code | The application product supplier shall qualify and document which protection from malicious code mechanisms are compatible with the application and note any special configu ration requirements. | Protection from malicious code (for example, viruses, worms, Trojan horses and spyware) may be provided by the control system application or by an external service or application. Control system appl ications need to be compatible with mechanisms designed to protect them from malicious code. This requirement does not imply that the product supplier is to qualify and document all malicious code protection mechanisms which are compatible with the application but implies that the product supplier is to qualify and document at least one mechanism. | The requirements for the four SL levels that relate to SAR 3.2 are: • SL-C(SI, component) 1: SAR 3.2 © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 • SL-C(SI, component) 2: SAR 3.2 • SL-C(SI, component) 3: SAR 3.2 • SL-C(SI, component) 4: SAR 3.2 13 Embedded device r equirements 13.1 Purpose The purpose of this set of requirements is to document requirements that are specific to embedded devices. | SR3.2 | SR 3.2 | Malicious code protection | The control system shall provide the capability to employ protection mechanisms to prevent, detect, report and mitigate the effects of malicious code or unauthorized software. The control system shall provide the capability to update the protection mechanisms. | The control system should us e protection mechanisms to prevent, detect, mitigate and report instances of detected malicious code (for example, viruses, worms, Trojan horses and spyware) transported by electronic mail, electronic mail attachments, Internet access, removable media (for example, universal serial bus (USB) devic es, diskettes or compact disks), PDF documents, web services, network connections and infected laptops or other common means. Detection mechanisms should be able to detect integrity violations of application binari es and data files. Techniques may include, but are not limited to, binary integrity and attributes monitoring, hashing and signature techniques. Mitigation techniques may include, but are not limited to, file cleaning, quarantining, file deletion, host communication restriction and IPSs. Prevention techniques may include, but are not limited to, application blacklisting and whitelisting techniques, removable media control, sandbox techniques and specific computing platforms mechanisms such as restricted firmware update capabilities, No Execute (NX) bit, data execution prevention (DEP), address space layout randomization (ASLR), stack corruption detection and mandatory access controls. See 10.4, SR 6.2 – Continuous monitoring for an associated requirement involving control system monitoring tools and techniques. Prevention and mitigation mechanisms may include those designed for host elements (such as computers and servers) and network -based mechanisms (such as IDS s and IPS s) and those mechanisms focused on control system specific components (such as PLCs and HMIs). | The requirements for the four SL levels that relate to SR 3.2 – Malicious code protectio n are: • SL-C(SI, control system) 1: SR 3.2 • SL-C(SI, control system) 2: SR 3.2 (1) • SL-C(SI, control system) 3: SR 3.2 (1) (2) • SL-C(SI, control system) 4: SR 3.2 (1) (2) | Same base identifier and enhancement sequence
74 | 2 | Base requirement | EDR2.4 | EDR 2.4 | EDR | Mobile code | In the event that an embedded device utilizes mobile code technologies, the embedded device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the embedded device: a) Control execution of mobile code; b) Control which users (human, software process, or device) are allowed to upload mobile code to the device; c) Control the execution of mobile code based on the results of an integrity check prior to the code being executed. | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, PDF, Postscript, Shockwave movies, Flash animations and VBScript. Usage restrictions apply to both the sel ection and use of mobile code installed on servers and mobile code downloaded and executed on individual workstations. Control procedures should prevent the development, acquisition or introduction of unacceptable mobile code within the control system in which the component resides. For example, mobile code exchanges may be disallowed directly with in the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to EDR 2.4 are: • SL-C(UC, component) 1: ED R 2.4 • SL-C(UC, component) 2: EDR 2.4 (1) • SL-C(UC, component) 3: EDR 2.4 (1) • SL-C(UC, component) 4: EDR 2.4 (1) | SR2.4 | SR 2.4 | Mobile code | The control system shall provide the capability to enforce usage restrictions for mobile code technologies based on the potential t o cause damage to the c ontrol system that includ e: a) preventing the execution of mobile code; b) requiring proper authentication and authorization for origin of the code; c) restricting mobile code transfer to/from the control system; and d) monitoring the use of mobile code. | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, portable document format (PDF), Postscript, Shockwave movies, F lash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and execut ed on individual workstations. Control procedures should preve nt the development, acquisition or introduction of unacceptabl e mobile code within the control system. For example, mobile code exchanges may be disallowed directly with the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to SR 2.4 – Mobile code are: • SL-C(UC, control system) 1: SR 2.4 • SL-C(UC, control system) 2: SR 2. 4 • SL-C(UC, control system) 3: SR 2. 4 (1) • SL-C(UC, control system) 4: SR 2. 4 (1) | Same base identifier and enhancement sequence
75 | 2 | Enhancement | EDR2.4.1 | EDR 2.4 RE (1) | EDR | Mobile code authenticity check | The embedded device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, PDF, Postscript, Shockwave movies, Flash animations and VBScript. Usage restrictions apply to both the sel ection and use of mobile code installed on servers and mobile code downloaded and executed on individual workstations. Control procedures should prevent the development, acquisition or introduction of unacceptable mobile code within the control system in which the component resides. For example, mobile code exchanges may be disallowed directly with in the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to EDR 2.4 are: • SL-C(UC, component) 1: ED R 2.4 • SL-C(UC, component) 2: EDR 2.4 (1) • SL-C(UC, component) 3: EDR 2.4 (1) • SL-C(UC, component) 4: EDR 2.4 (1) | SR2.4.1 | SR 2.4 RE (1) | Mobile code integrity check | The control system shall provide the capability to verify integrity of the mobile code before allowing code execution. 6.6.3.2 Void | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, portable document format (PDF), Postscript, Shockwave movies, F lash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and execut ed on individual workstations. Control procedures should preve nt the development, acquisition or introduction of unacceptabl e mobile code within the control system. For example, mobile code exchanges may be disallowed directly with the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to SR 2.4 – Mobile code are: • SL-C(UC, control system) 1: SR 2.4 • SL-C(UC, control system) 2: SR 2. 4 • SL-C(UC, control system) 3: SR 2. 4 (1) • SL-C(UC, control system) 4: SR 2. 4 (1) | Same base identifier and enhancement sequence
76 | 2 | Base requirement | EDR2.13 | EDR 2.13 | EDR | Use of physical diagnostic and test interfac es | Embedded devices shall protect against unauthorized use of the physical factory diagnostic and test interface(s) (e.g. JTAG debugging). © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | Factory diagnostic and test interface(s) are created at various locations within the embedded device to assist the embedded device’s developers and factory personnel as they test the functional implementation, and when errors are discovered to subsequently remove them from the embedded device. However, these same interfaces should be carefully protected from access by unauthorized entities to protect the essential functionality provided by the embedded device to the IACS. If a diagnostic and test interface does not provide an ability to control the embedded device or to access non- public information, then it will not need an authentication mechanism. This shall be determined via a threat and risk assessment. An example of this would be JTAG debugging, in whi ch JTAG is used to take control of the processor and execute arbitrary commands, versus a JTAG boundary scan where JTAG is used to simply read information (which may be publicly available information). There may be cases where the factory diagnostic and test interface(s) use network communications with the device. When this is the case those interfaces are to be subjected to all of the requirements of this document. | The requirements for the four SL levels that relate to EDR 2.13 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: EDR 2.13 • SL-C(SI, component) 3: EDR 2.13 (1) • SL-C(SI, component) 4: EDR 2.13 (1) | [6 empty] | No corresponding SR
77 | 2 | Enhancement | EDR2.13.1 | EDR 2.13 RE (1) | EDR | Active monitoring | Embedded devices shall provide active monitoring of the device’s diagnostic and test interface(s) and generate an audit log entry when attempts to access these interface(s) are detected. | Factory diagnostic and test interface(s) are created at various locations within the embedded device to assist the embedded device’s developers and factory personnel as they test the functional implementation, and when errors are discovered to subsequently remove them from the embedded device. However, these same interfaces should be carefully protected from access by unauthorized entities to protect the essential functionality provided by the embedded device to the IACS. If a diagnostic and test interface does not provide an ability to control the embedded device or to access non- public information, then it will not need an authentication mechanism. This shall be determined via a threat and risk assessment. An example of this would be JTAG debugging, in whi ch JTAG is used to take control of the processor and execute arbitrary commands, versus a JTAG boundary scan where JTAG is used to simply read information (which may be publicly available information). There may be cases where the factory diagnostic and test interface(s) use network communications with the device. When this is the case those interfaces are to be subjected to all of the requirements of this document. | The requirements for the four SL levels that relate to EDR 2.13 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: EDR 2.13 • SL-C(SI, component) 3: EDR 2.13 (1) • SL-C(SI, component) 4: EDR 2.13 (1) | [6 empty] | No corresponding SR
78 | 3 | Base requirement | EDR3.2 | EDR 3.2 | EDR | Protection from malicious code | The embedded device shall provide the capability to protect from installation and execution of unauthorized software. | Unauthorized software may contain malicious code and thus be harmful to the component. If an embedded device is able to utilize a compensating control, it need not di rectly support protection from malicious code. It is assumed that the IACS will be responsible for providing the required safeguards. However, for scenarios such as having a local universal serial bus (USB) host access, the need for protection from malicio us code should be determined by a risk assessment. Detection mechanisms should be able to detect integrity violations of application binaries and data files. Techniques may include, but are not limited to, binary integrity and attributes monitoring, hashing and signature techniques. Prevention techniques may include, but are not limited to, removable media control, sandbox techniques and specific computing platforms mechanisms such as restricted firmware update capabilities, No Execute (NX) bit, data execut ion prevention (DEP), address space layout © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 randomization (ASLR), stack corruption detection and mandatory access controls. See 10.4 for an associated requirement i nvolving control system monitoring tools and techniques. | The requirements for the four SL levels that relate to EDR 3.2 are: • SL-C(SI, component) 1: EDR 3.2 • SL-C(SI, component) 2: EDR 3.2 • SL-C(SI, component) 3: EDR 3.2 • SL-C(SI, component) 4: EDR 3.2 | SR3.2 | SR 3.2 | Malicious code protection | The control system shall provide the capability to employ protection mechanisms to prevent, detect, report and mitigate the effects of malicious code or unauthorized software. The control system shall provide the capability to update the protection mechanisms. | The control system should us e protection mechanisms to prevent, detect, mitigate and report instances of detected malicious code (for example, viruses, worms, Trojan horses and spyware) transported by electronic mail, electronic mail attachments, Internet access, removable media (for example, universal serial bus (USB) devic es, diskettes or compact disks), PDF documents, web services, network connections and infected laptops or other common means. Detection mechanisms should be able to detect integrity violations of application binari es and data files. Techniques may include, but are not limited to, binary integrity and attributes monitoring, hashing and signature techniques. Mitigation techniques may include, but are not limited to, file cleaning, quarantining, file deletion, host communication restriction and IPSs. Prevention techniques may include, but are not limited to, application blacklisting and whitelisting techniques, removable media control, sandbox techniques and specific computing platforms mechanisms such as restricted firmware update capabilities, No Execute (NX) bit, data execution prevention (DEP), address space layout randomization (ASLR), stack corruption detection and mandatory access controls. See 10.4, SR 6.2 – Continuous monitoring for an associated requirement involving control system monitoring tools and techniques. Prevention and mitigation mechanisms may include those designed for host elements (such as computers and servers) and network -based mechanisms (such as IDS s and IPS s) and those mechanisms focused on control system specific components (such as PLCs and HMIs). | The requirements for the four SL levels that relate to SR 3.2 – Malicious code protectio n are: • SL-C(SI, control system) 1: SR 3.2 • SL-C(SI, control system) 2: SR 3.2 (1) • SL-C(SI, control system) 3: SR 3.2 (1) (2) • SL-C(SI, control system) 4: SR 3.2 (1) (2) | Same base identifier and enhancement sequence
79 | 3 | Base requirement | EDR3.10 | EDR 3.10 | EDR | Support for updates | The embedded device shall support the ability to be updated and upgraded. | Embedded devices over their installed lifetime may have the need for installation of updates and upgrades. There will be cases where embedded devices are supporting or executing essential functions as well. When this is the case the embedded device needs to have mechanisms in place to support patching and updating without impacting the essential functions of high availability systems (see 4.2). One example for providing this capability would be to support redundancy within the embedded device. | The requirem ents for the four SL levels that relate to E DR 3.10 are: • SL-C(SI, component) 1: EDR 3.10 • SL-C(SI, component) 2: EDR 3.10 (1) • SL-C(SI, component) 3: EDR 3.10 (1) • SL-C(SI, component) 4: EDR 3.10 (1) | [6 empty] | No corresponding SR
80 | 3 | Enhancement | EDR3.10.1 | EDR 3.10 RE (1) | EDR | Update authenticity and integrity | The embedded device shall validate the authenticity and integrity of any software update or upgrade prior to installation. | Embedded devices over their installed lifetime may have the need for installation of updates and upgrades. There will be cases where embedded devices are supporting or executing essential functions as well. When this is the case the embedded device needs to have mechanisms in place to support patching and updating without impacting the essential functions of high availability systems (see 4.2). One example for providing this capability would be to support redundancy within the embedded device. | The requirem ents for the four SL levels that relate to E DR 3.10 are: • SL-C(SI, component) 1: EDR 3.10 • SL-C(SI, component) 2: EDR 3.10 (1) • SL-C(SI, component) 3: EDR 3.10 (1) • SL-C(SI, component) 4: EDR 3.10 (1) | [6 empty] | No corresponding SR
81 | 3 | Base requirement | EDR3.11 | EDR 3.11 | EDR | Physical tamper resistance and d etection | The embedded device shall provide tamper resistance and detection mechanisms to protect against unauthorized physical access into the device. | The purpose of tamper resistance mechanisms is to prevent an attem pt by an attacker to execute an unauthorized physical action against an IACS device. Secondary to prevention, detection and response are essential should a tampering event occur. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 Tamper resistance mechanisms are most effectively used in combinations to prevent access to any critical components. Tamper resistance consists of using specialized materials to make tampering of a device or module difficult. This can include such features as hardened enclosures, locks, encapsulation, or security screws. Putting in place tight airflow paths will increase the difficulty of probing the product inter nals. The purpose of tamper evidence is to ensure that visible or electronic evidence remains when a tampering event occurs. Many simple evidence techniques are comprised o f seals and tapes to make it obvious that there has been physical tampering. More sophisticated techniques include switches. | The requirements for the four SL levels that relate to EDR 3.11 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: EDR 3.11 • SL-C(SI, component) 3: EDR 3.11 (1) • SL-C(SI, component) 4: EDR 3.11 (1) | [6 empty] | No corresponding SR
82 | 3 | Enhancement | EDR3.11.1 | EDR 3.11 RE (1) | EDR | Notification of a tampering attempt | The embedded device shall be capable of automatically providing notification to a configurable set of recipients upon discovery of an attempt to make an unauthorized physical access. All notifications of tampering shall be logged as part of the overall audit logging function. | The purpose of tamper resistance mechanisms is to prevent an attem pt by an attacker to execute an unauthorized physical action against an IACS device. Secondary to prevention, detection and response are essential should a tampering event occur. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 Tamper resistance mechanisms are most effectively used in combinations to prevent access to any critical components. Tamper resistance consists of using specialized materials to make tampering of a device or module difficult. This can include such features as hardened enclosures, locks, encapsulation, or security screws. Putting in place tight airflow paths will increase the difficulty of probing the product inter nals. The purpose of tamper evidence is to ensure that visible or electronic evidence remains when a tampering event occurs. Many simple evidence techniques are comprised o f seals and tapes to make it obvious that there has been physical tampering. More sophisticated techniques include switches. | The requirements for the four SL levels that relate to EDR 3.11 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: EDR 3.11 • SL-C(SI, component) 3: EDR 3.11 (1) • SL-C(SI, component) 4: EDR 3.11 (1) | [6 empty] | No corresponding SR
83 | 3 | Base requirement | EDR3.12 | EDR 3.12 | EDR | Provisioning product supplier roots of trust | Embedded device s shall provide the capability to provision and protect the confidentiality, integrity, and authenticity of product supplier keys and data to be used as one or more “roots of trust” at the time of manufacture of the device. | In order for a component to be able to validate the authenticity and integrity of the hardware, software, and data provided by the product supplier, it should possess a trusted source of data to perform the validation process. This trusted source of data is referred to as the “root of trust” for the system. This trusted source of data may be a set of cryptographic hashes of “known good” software, or it may be the public portion of an asymmetric cryptographic key pair to be used in the validation of cryptographic signatures. This trusted data is often used to validate critical software, firmware, and data prior to booting the firmware or operating system of a component, in order to validate that the component will boot into a “known good” state in which all security mechanisms are known to be operational and uncompromised. “Root of trust” data is often protected via hardware mechanisms, preventing any modification of the data during normal operations of the component. Modification of product supplier root of trust data is typically limited to the product supplier’s provisioning process, where the product supplier has a trusted process to perform the provisioning of the data. Instead, information to be validated against the root of trust is submitted to the validation process through a hardware or software API which performs the validation and returns the results without exposing the protected data. | [7 empty] | No corresponding SR
84 | 3 | Base requirement | EDR3.13 | EDR 3.13 | EDR | Provisioning asset owner roots of trust | Embedded device s shall a) provide the capability to provision and protect the confidentiality, integrity, and authenticity of asset owner keys and data to be used as “roots of trust”; and b) support the capability to provision without reliance on components that may be outside of the device ’s security zone. | and supplemental g uidance Product suppliers have established mechanisms to ensure that the software and firmware on their components is authentic, and the integrity of that software and firmware has not been compromised. This allows the product supplier to provide the asset owner with a “known good” state from which to operate. However, many product suppliers also provide mechanisms for asset owners to extend the functionality of their devices through the use of mobile code, user programs, or other such means. In order to protect the security of the component, it is important that these extensions to the component’s functionality also be validated to ensure that they are authorized, and that the asset owner has approved of their origins. In order to perform these validations, the component should contain data that provides a way to differentiate between valid and invalid origins. The list of valid and invalid origins will differ from asset owner to asset owner, and it is unlikely that a product supplier will have a complete list of every possible valid origin at time of manufacture. Therefore, it is important that the product supplier provide a way for the asset owner to securely provision their own “roots of trust” which pr ovide the ability to distinguish between origins allowed by the asset owner’s security policy, and those that are not. The authenticity and integrity of these “roots of trust” should be protected so that malicious actors cannot add additional roots of trus t that grant them the ability to operate on the component. A root of trust can also be used as a basis communications security, such as communications integrity required by CR 3.1 – Communication integrity (7.3) or communications confidentiality required by CR 4.1 – Information confidentiality (8.3). Requirements such as EDR 2.4 – Mobile code (13.2) require the component to complete authenticity checks on mobile code prior to the execution of mobile code. The roots of trust provided by this requirement provide the data necessary to validate the origin and integrity of mobile code, allowing the component to independently determine if the code is allowed to execute. 13.8.3 Requirement enhancemen ts None | The requirements for the four SL levels that relate to EDR 3.13 are: © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: EDR 3.13 • SL-C(SI, component) 3: EDR 3.13 • SL-C(SI, component) 4: EDR 3.13 | [6 empty] | No corresponding SR
85 | 3 | Base requirement | EDR3.14 | EDR 3.14 | EDR | Integrity of the boot process | Embedded devices shall verif y the integrity of the firmware, software, and configuration data needed for the component’s boot and runtime processes prior to use. | and supplemental g uidance In order to make assurances to an asset owner that a component’s security functionality has not been compromised, it is necessary to ensure that the component’s software and firmware has not been tampered with, and that the software and firmware is valid to execute on the component. Therefore, the component should perform checks to validate the integrity of the component’s firmware and/or software prior to use during the boot process, to ensure that the component does not boot into an insecure or invalid operating state that could damage the component or provide a path for a malicious actor to gain access to additional components, assets, or data. | The requirements for the four SL levels that relate to EDR 3.14 are: • SL-C(SI, component) 1: EDR 3.14 • SL-C(SI, component) 2: EDR 3.14 (1) • SL-C(SI, component) 3: EDR 3.14 (1) • SL-C(SI, component) 4: EDR 3.14 (1) 14 Host device requirements 14.1 Purpose The purpose of this set of requirements is to document requirements that are specific t o host devices. 14.2 HD R 2.4 – Mobile code 14.2.1 Requirement In the event that a host device utilizes mobile code technologies, that host device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the host device: a) control execution of mobile code; b) control which users (human, software process, or device) are allowed to upload mobile code to the host device; and © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 c) control the code execution based upon integrity checks on the mobile code and prior to the code being executed. 14.2.2 Rationale and supplemental guidance Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, PDF, Postscript, Shockwave movies, Flash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and executed on individual workstations. Control procedures should prevent the development, acquisition or introduction of unacceptable mobile code within the control system in which the host device resides. For example, mobile code exchanges may be disallowed d irectly with the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. Mobile code could be secured by adding integrity, authenticity, and authorization checks to the code itself (application layer), or for “just-in-time” code execution through transmitting the mobile code via a secure communications tunnel which provides these attributes, or any mechanism equivalent to these options. 14.2.3 Requirement enhancements (1) Mobile code authenticity check The host device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. 14.2.4 Security levels The requirements for the four SL le vels that relate to HDR 2.4 are: • SL-C(UC, component) 1: HD R 2.4 • SL-C(UC, component) 2: HDR 2.4(1) • SL-C(UC, component) 3: HDR 2.4 (1) • SL-C(UC, component) 4: HDR 2.4 (1) | [6 empty] | No corresponding SR
86 | 3 | Enhancement | EDR3.14.1 | EDR 3.14 RE (1) | EDR | Authenticity of the boot process | Embedded devices shall use the component’s product supplier roots of trust to veri fy the authenticity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. | and supplemental g uidance In order to make assurances to an asset owner that a component’s security functionality has not been compromised, it is necessary to ensure that the component’s software and firmware has not been tampered with, and that the software and firmware is valid to execute on the component. Therefore, the component should perform checks to validate the integrity of the component’s firmware and/or software prior to use during the boot process, to ensure that the component does not boot into an insecure or invalid operating state that could damage the component or provide a path for a malicious actor to gain access to additional components, assets, or data. | The requirements for the four SL levels that relate to EDR 3.14 are: • SL-C(SI, component) 1: EDR 3.14 • SL-C(SI, component) 2: EDR 3.14 (1) • SL-C(SI, component) 3: EDR 3.14 (1) • SL-C(SI, component) 4: EDR 3.14 (1) 14 Host device requirements 14.1 Purpose The purpose of this set of requirements is to document requirements that are specific t o host devices. 14.2 HD R 2.4 – Mobile code 14.2.1 Requirement In the event that a host device utilizes mobile code technologies, that host device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the host device: a) control execution of mobile code; b) control which users (human, software process, or device) are allowed to upload mobile code to the host device; and © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 c) control the code execution based upon integrity checks on the mobile code and prior to the code being executed. 14.2.2 Rationale and supplemental guidance Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, PDF, Postscript, Shockwave movies, Flash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and executed on individual workstations. Control procedures should prevent the development, acquisition or introduction of unacceptable mobile code within the control system in which the host device resides. For example, mobile code exchanges may be disallowed d irectly with the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. Mobile code could be secured by adding integrity, authenticity, and authorization checks to the code itself (application layer), or for “just-in-time” code execution through transmitting the mobile code via a secure communications tunnel which provides these attributes, or any mechanism equivalent to these options. 14.2.3 Requirement enhancements (1) Mobile code authenticity check The host device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. 14.2.4 Security levels The requirements for the four SL le vels that relate to HDR 2.4 are: • SL-C(UC, component) 1: HD R 2.4 • SL-C(UC, component) 2: HDR 2.4(1) • SL-C(UC, component) 3: HDR 2.4 (1) • SL-C(UC, component) 4: HDR 2.4 (1) | [6 empty] | No corresponding SR
87 | 2 | Base requirement | HDR2.13 | HDR 2.13 | HDR | Use of physical diagnostic and test interfaces | Host devices shall protect against unauthorized use of the physical factory diagnostic and test interface(s) (e.g. JTAG debugging). | Factory diagnostic and test interface(s) are created at various locations within the host device to assist the component’s developers and factory personnel as they test the functional implementation, and when errors are discovered to subsequently remove them from the component. However, these same interfaces should be carefully protected from access by unauthorized entities to protect the essential functionality provided by the component to the IACS. There may be cases where the factory diagnostic and test interface(s) use network communications with the device. When this is the case those interfaces are to be subjected to all of the requirements of this document. If a diagnostic and test interface does not provide an ability to control the host device or to access non -public information, then it will not need an authentication mechanism. This shall be determined via a threat and risk assessment. An example of this would be JTAG debugging, in which JTAG is used to take control of the processor and execute arbitrary © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 commands, versus a JTAG boundary scan where JTAG is used to simply read information (which may be publicly available information). | The requirements for the four SL levels that relate to HDR 2.13 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: HDR 2.13 • SL-C(SI, component) 3: HDR 2.13 (1) • SL-C(SI, component) 4: HDR 2.13 (1) | [6 empty] | No corresponding SR
88 | 2 | Enhancement | HDR2.13.1 | HDR 2.13 RE (1) | HDR | Active monitoring | Host devices shall provide active monitoring of the device’s diagnostic and test interface(s) and generate an audit log entry when attempts to access these interface(s) are detected. | Factory diagnostic and test interface(s) are created at various locations within the host device to assist the component’s developers and factory personnel as they test the functional implementation, and when errors are discovered to subsequently remove them from the component. However, these same interfaces should be carefully protected from access by unauthorized entities to protect the essential functionality provided by the component to the IACS. There may be cases where the factory diagnostic and test interface(s) use network communications with the device. When this is the case those interfaces are to be subjected to all of the requirements of this document. If a diagnostic and test interface does not provide an ability to control the host device or to access non -public information, then it will not need an authentication mechanism. This shall be determined via a threat and risk assessment. An example of this would be JTAG debugging, in which JTAG is used to take control of the processor and execute arbitrary © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 commands, versus a JTAG boundary scan where JTAG is used to simply read information (which may be publicly available information). | The requirements for the four SL levels that relate to HDR 2.13 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: HDR 2.13 • SL-C(SI, component) 3: HDR 2.13 (1) • SL-C(SI, component) 4: HDR 2.13 (1) | [6 empty] | No corresponding SR
89 | 3 | Base requirement | HDR3.2 | HDR 3.2 | HDR | Protection from malicious code | There shall be mechanisms on host devices that are qualified by the IACS product supplier to provide protection from malicious code. The IACS product supplier shall document any special configuration requirements related to protection from malicious code. | Host devices need to support the use of malicious code protection (against, for example, viruses, worms, Trojan horses and spyware). The product supplier should qualify and document the configuration of protection from malicious code mechanisms so that the primary mission of t he control system is maintained. | The requirements for the four SL levels that relate to HD R 3.2 are: • SL-C(SI, component) 1: HDR 3.2 • SL-C(SI, component) 2: HDR 3.2 (1) • SL-C(SI, component) 3: HDR 3.2 (1) • SL-C(SI, component) 4: HDR 3.2 (1) | SR3.2 | SR 3.2 | Malicious code protection | The control system shall provide the capability to employ protection mechanisms to prevent, detect, report and mitigate the effects of malicious code or unauthorized software. The control system shall provide the capability to update the protection mechanisms. | The control system should us e protection mechanisms to prevent, detect, mitigate and report instances of detected malicious code (for example, viruses, worms, Trojan horses and spyware) transported by electronic mail, electronic mail attachments, Internet access, removable media (for example, universal serial bus (USB) devic es, diskettes or compact disks), PDF documents, web services, network connections and infected laptops or other common means. Detection mechanisms should be able to detect integrity violations of application binari es and data files. Techniques may include, but are not limited to, binary integrity and attributes monitoring, hashing and signature techniques. Mitigation techniques may include, but are not limited to, file cleaning, quarantining, file deletion, host communication restriction and IPSs. Prevention techniques may include, but are not limited to, application blacklisting and whitelisting techniques, removable media control, sandbox techniques and specific computing platforms mechanisms such as restricted firmware update capabilities, No Execute (NX) bit, data execution prevention (DEP), address space layout randomization (ASLR), stack corruption detection and mandatory access controls. See 10.4, SR 6.2 – Continuous monitoring for an associated requirement involving control system monitoring tools and techniques. Prevention and mitigation mechanisms may include those designed for host elements (such as computers and servers) and network -based mechanisms (such as IDS s and IPS s) and those mechanisms focused on control system specific components (such as PLCs and HMIs). | The requirements for the four SL levels that relate to SR 3.2 – Malicious code protectio n are: • SL-C(SI, control system) 1: SR 3.2 • SL-C(SI, control system) 2: SR 3.2 (1) • SL-C(SI, control system) 3: SR 3.2 (1) (2) • SL-C(SI, control system) 4: SR 3.2 (1) (2) | Same base identifier and enhancement sequence
90 | 3 | Enhancement | HDR3.2.1 | HDR 3.2 RE (1) | HDR | Report version of code protection | The host device shall automatically report the software and file versions of protection from malicious code in use (as part of overall logging function). | Host devices need to support the use of malicious code protection (against, for example, viruses, worms, Trojan horses and spyware). The product supplier should qualify and document the configuration of protection from malicious code mechanisms so that the primary mission of t he control system is maintained. | The requirements for the four SL levels that relate to HD R 3.2 are: • SL-C(SI, component) 1: HDR 3.2 • SL-C(SI, component) 2: HDR 3.2 (1) • SL-C(SI, component) 3: HDR 3.2 (1) • SL-C(SI, component) 4: HDR 3.2 (1) | SR3.2.1 | SR 3.2 RE (1) | Malicious code protection on entry and exit points | The control system shall provide the capability to employ m alicious code protection mechanisms at all entry and exit points. NOTE Such mechanisms are commonly provided on removable media, firewalls, unidirectional gateways, web servers, proxy servers or remote -access servers. | The control system should us e protection mechanisms to prevent, detect, mitigate and report instances of detected malicious code (for example, viruses, worms, Trojan horses and spyware) transported by electronic mail, electronic mail attachments, Internet access, removable media (for example, universal serial bus (USB) devic es, diskettes or compact disks), PDF documents, web services, network connections and infected laptops or other common means. Detection mechanisms should be able to detect integrity violations of application binari es and data files. Techniques may include, but are not limited to, binary integrity and attributes monitoring, hashing and signature techniques. Mitigation techniques may include, but are not limited to, file cleaning, quarantining, file deletion, host communication restriction and IPSs. Prevention techniques may include, but are not limited to, application blacklisting and whitelisting techniques, removable media control, sandbox techniques and specific computing platforms mechanisms such as restricted firmware update capabilities, No Execute (NX) bit, data execution prevention (DEP), address space layout randomization (ASLR), stack corruption detection and mandatory access controls. See 10.4, SR 6.2 – Continuous monitoring for an associated requirement involving control system monitoring tools and techniques. Prevention and mitigation mechanisms may include those designed for host elements (such as computers and servers) and network -based mechanisms (such as IDS s and IPS s) and those mechanisms focused on control system specific components (such as PLCs and HMIs). | The requirements for the four SL levels that relate to SR 3.2 – Malicious code protectio n are: • SL-C(SI, control system) 1: SR 3.2 • SL-C(SI, control system) 2: SR 3.2 (1) • SL-C(SI, control system) 3: SR 3.2 (1) (2) • SL-C(SI, control system) 4: SR 3.2 (1) (2) | Same base identifier and enhancement sequence
91 | 3 | Base requirement | HDR3.10 | HDR 3.10 | HDR | Support for updates | Host devi ces shall support the ability to be updated and upgraded. | Host devices over their installed lifetime may have the need for installation of updates and upgrades. There will be cases where host devices are supporting or executing essential © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 functions as well. When this is the case the host device should have mechanisms in place to support patching and updating without impacting the essential function s of high availability systems (see 4.2). One example for providing this capability would be to support redundancy within the host device. | The requirements for the four SL levels that relate to HDR 3.10 are: • SL-C(SI, component) 1: HDR 3.10 • SL-C(SI, component) 2: HDR 3.10 (1) • SL-C(SI, component) 3: HDR 3.10 (1) • SL-C(SI, component) 4: HDR 3.10 (1) | [6 empty] | No corresponding SR
92 | 3 | Enhancement | HDR3.10.1 | HDR 3.10 RE (1) | HDR | Update authen ticity and integrity | Host devices shall validate the authenticity and integrity of any software update or upgrade prior to installation. | Host devices over their installed lifetime may have the need for installation of updates and upgrades. There will be cases where host devices are supporting or executing essential © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 functions as well. When this is the case the host device should have mechanisms in place to support patching and updating without impacting the essential function s of high availability systems (see 4.2). One example for providing this capability would be to support redundancy within the host device. | The requirements for the four SL levels that relate to HDR 3.10 are: • SL-C(SI, component) 1: HDR 3.10 • SL-C(SI, component) 2: HDR 3.10 (1) • SL-C(SI, component) 3: HDR 3.10 (1) • SL-C(SI, component) 4: HDR 3.10 (1) | [6 empty] | No corresponding SR
93 | 3 | Base requirement | HDR3.11 | HDR 3.11 | HDR | Physical tamper resistance and detection | Host devices shall provide the capability to support tamper resistance and detection mechanisms to protect against unauthorized physical access into the device. | The purpose of tamper resistance mechanisms is to prevent an attempt by an attacker to execute an unauthorized physical action against an IACS device. Secondary to prevention, detection and response are essential should a tampering event occur. Tamper resistance mechanisms are most effectively used in combinations to prevent access to any critical components. Tamper resistance consists of using specialized materials to make tampering of a device or module difficult. This can include such features as hardened enclosures, locks, encapsulation, or security screws. Putting in place tight airflow paths will increase the d ifficulty of probing the product inter nals. The purpose of tamper evidence is to ensure that visible or electronic evidence remains when a tampering event occurs. Many simple evidence techniques are comprised of seals and tapes to make it obvious that there has been physical tampering. More sophisticated techniques include switches. | The requirements for the four SL levels that relate to HDR 3.11 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: HDR 3.11 • SL-C(SI, component) 3: HDR 3.11 (1) • SL-C(SI, component) 4: HDR 3.11 (1) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | [6 empty] | No corresponding SR
94 | 3 | Enhancement | HDR3.11.1 | HDR 3.11 RE (1) | HDR | Notification of a tampering attempt | Host devices shall be capable of automatically providing notification to a configurable set of recipients upon discovery of an attempt to make an unauthorized physical access. All notifications of tampering shall be logged as part of the overall audit logging function. | The purpose of tamper resistance mechanisms is to prevent an attempt by an attacker to execute an unauthorized physical action against an IACS device. Secondary to prevention, detection and response are essential should a tampering event occur. Tamper resistance mechanisms are most effectively used in combinations to prevent access to any critical components. Tamper resistance consists of using specialized materials to make tampering of a device or module difficult. This can include such features as hardened enclosures, locks, encapsulation, or security screws. Putting in place tight airflow paths will increase the d ifficulty of probing the product inter nals. The purpose of tamper evidence is to ensure that visible or electronic evidence remains when a tampering event occurs. Many simple evidence techniques are comprised of seals and tapes to make it obvious that there has been physical tampering. More sophisticated techniques include switches. | The requirements for the four SL levels that relate to HDR 3.11 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: HDR 3.11 • SL-C(SI, component) 3: HDR 3.11 (1) • SL-C(SI, component) 4: HDR 3.11 (1) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | [6 empty] | No corresponding SR
95 | 3 | Base requirement | HDR3.12 | HDR 3.12 | HDR | Provisioning product supplier roots of trust | Host devices shall provide the capability to provision and protect the confidentiality, integrity, and authenticity of product supplier keys and data to be used as one or more “roots of trust” at the time of manufacture of the device. | In order for a component to be able to validate the authenticity and integrity of the hardware, software, and data provided by the product supplier, it should possess a trusted source of data to perform the validation process. This trusted source of data i s referred to as the “root of trust” for the system. This trusted source of data may be a set of cryptographic hashes of “known good” software, or it may be the public portion of an asymmetric cryptographic key pair to be used in the validation of cryptogr aphic signatures. This trusted data is often used to validate critical software, firmware, and data prior to booting the firmware or operating system of a component, in order to validate that the component will boot into a “known good” state in which all s ecurity mechanisms are known to be operational and uncompromised. “Root of trust” data can be protected by software or hardware implemented mechanisms to prevent any modification of the data during normal operations of the component. Modification of produc t supplier root of trust data is typically limited to the product supplier’s provisioning process, where the product supplier has a trusted process to perform the provisioning of the data. Instead, information to be validated against the root of trust is s ubmitted to the validation process through a hardware or software API which performs the validation and returns the results without exposing the protected data. | The requirements for the four SL levels that rel ate to HDR 3.12 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: HDR 3.12 • SL-C(SI, component) 3: HDR 3.12 • SL-C(SI, component) 4: HDR 3.12 | [6 empty] | No corresponding SR
96 | 3 | Base requirement | HDR3.13 | HDR 3.13 | HDR | Provisioning asset owner roots of trust | Host devices shall a) provide the capability to provision and protect the confidentiality, integrity, and authenticity of asset owner keys and data to be used as “roots of trust”; and b) support the capability to provision without reliance on components that may be outside of the device’s security z one. | Product suppliers have established mechanisms to ensure that the software and firmware on their components is authentic, and the integrity of that software and firmware has not been compromised. This allows the pro duct supplier to provide the asset owner with a “known good” state from which to operate. However, many product suppliers also provide mechanisms for asset owners to extend the functionality of their devices through the use of mobile code, user programs, or other such means. In order to protect the security of the component, it is important that these extensions to the component’s functionality also be © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 validated to ensure that they are authorized, and that the asset owner has approved of their origins. In order to perform these validations, the component should contain data that provides a way to differentiate between valid and invalid origins. The list of valid and invalid origins will differ from asset owner to asset owner, and it is unlikely that a produc t supplier will have a complete list of every possible valid origin at time of manufacture. Therefore, it is important that the product supplier provide a way for the asset owner to securely provision their own “roots of trust” which provide the ability to distinguish between origins allowed by the asset owner’s security policy, and those that are not. The authenticity and integrity of these “roots of trust” should be protected so that malicious actors cannot add additional roots of trust that grant them the ability to operate on the component. Requirements such as HDR 2.4 – Mobile code (14.2) require the component to complete authenticity checks on mobile code prior to the execution of mobile code. The roots of trust provided by this requirement provide the data necessary to validate the origin and integrity of mobile code, allowing the component to independently determine if the code is allowed to execute. A root of trust can also be used as a basis communications security, such as communications integrity require d by CR 3.1 – Communication integrity (7.3) or communications confidentiality required by CR 4.1 – Information confidentiality (8.3). | The requirements for the four SL levels that relate to HDR 3.13 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: HDR 3.13 • SL-C(SI, component) 3: HDR 3.13 • SL-C(SI, component) 4: HDR 3.13 | [6 empty] | No corresponding SR
97 | 3 | Base requirement | HDR3.14 | HDR 3.14 | HDR | Integrity of the boot process | Host devices shall verify the integrity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. | In order to make assurances to an asset owner that a component’s security functionality has not been compromised, it is necessary to ensure that the component’s software and firmware has not been tampered with, and that the software and firmware is valid to execute on the component. Therefore, the component should perform checks to validate the integrity and authenticity of the component’s firmware and/or software prior to the boot process, to ensure that the component does not boot into an insecure or invalid operating state that could damage the com ponent or provide a path for a malicious actor to gain access to additional components, assets, or data. | The requirements for the four SL levels that relate to HDR 3.14 are: • SL-C(SI, component) 1: HDR 3.14 • SL-C(SI, component) 2: HDR 3.14 (1) • SL-C(SI, component) 3: HDR 3.14 (1) • SL-C(SI, component) 4: HDR 3.14 (1) 15 Network device requirements 15.1 Purpose The purpose of this set of requirements is to document requirements that are specific to network devices. 15.2 ND R 1.6 – Wireless access management 15.2.1 Requirement A network device supporting wireless access management shall provide the capability to identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. 15.2.2 Rationale and supplemental guidance Any wireless technology can, and in most cases should, be considered as just another communication protocol option. T hus, it should be subject to the same IACS security requirements as any other communication type utilized by the IACS. However, from a security point of view, there is at least one significant difference between wi red and wireless communications. Physical security counterm easures are typically less effective when using wireless. 15.2.3 Requirement enhancements (1) Unique identification and authentication The network device shall provide the capability to uniquely identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. 15.2.4 Security levels The requirements for the four SL levels that relate to ND R 1.6 are: • SL-C(UC, component) 1: ND R 1.6 • SL-C(UC, component) 2: ND R 1.6 (1) • SL-C(UC, component) 3: ND R 1.6 (1) • SL-C(UC, component) 4: ND R 1.6 (1) 15.3 ND R 1.13 – Access via untrusted networks 15.3.1 Requirement The network device supporting device access into a network shall provide the capability to monitor and control all methods of access to the network device via untrusted networks. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 15.3.2 Rationale and supplemental guidance The network device should protect against unauthorized connections or subversion of authorized connections. Examples of access to the network device via untrusted networks typically include remote access methods (such as, dial -up, broadband and wireless) as well as connections from a company’s office (non- control system) network. The network device may provide ACL (access control list) functionality to restrict access by: Layer 2 forwarding devices such as Ethernet swi tches: a) MAC address b) VLAN Layer 3 forwarding devices such as routers, gateways and firewalls: a) IP address b) port and protocol c) virtual private networks 15.3.3 Requirement enhancements (1) Explicit access request approval The network device shall provide the capability to deny access requests via untrusted networks unless explicitly approved by an assigned role. 15.3.4 Security levels The requirements for the four SL levels that relate to ND R 1.13 are: • SL-C(UC, component) 1: ND R 1.13 • SL-C(UC, component) 2: ND R 1.13 • SL-C(UC, component) 3: ND R 1.13 (1) • SL-C(UC, component) 4: ND R 1.13 (1) 15.4 ND R 2.4 – Mobile code 15.4.1 Requirement In the event that a network device utilizes mobile code technologies, the network device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the network device: a) control execution of mobile code; b) control which users (human, software process, or device) are allowed to transfer mobile code to/from the network device; and c) control the code execution based upon integrity checks on mobile code and prior to the code being executed 15.4.2 Rationale and supplemental guidance Mobile c ode technologies include, but are not limited to, Java, JavaScript, ActiveX, PDF, Postscript, Shockwave movies, Flash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and executed on individual workstations. Control procedures should prevent the development, acquisition or introduction of unacceptable mobile code within the control system in which the component resides. For example, mobile code exchanges may be disallowed directly with in © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. Mobile code could be secured by adding integrity, authenticity, and authorization checks to the code itself (application layer), or for “just -in-time” code execution through transmitting the mobile code via a secure communications tunnel which provides these attributes, or any mechanism equivalent to these options. 15.4.3 Requirement enhancements (1) Mobile code authenticity check The network device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. 15.4.4 Security levels The requirements for the four SL levels that relate to NDR 2.4 are: • SL-C(UC, component) 1: ND R 2.4 • SL-C(UC, component) 2: NDR 2.4 (1) • SL-C(UC, component) 3: NDR 2.4 (1) • SL-C(UC, component) 4: NDR 2.4 (1) | [6 empty] | No corresponding SR
98 | 3 | Enhancement | HDR3.14.1 | HDR 3.14 RE (1) | HDR | Authenticity of the boot process | © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 Host devices shall use the component’s product supplier roots of trust to veri fy the authenticity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. | In order to make assurances to an asset owner that a component’s security functionality has not been compromised, it is necessary to ensure that the component’s software and firmware has not been tampered with, and that the software and firmware is valid to execute on the component. Therefore, the component should perform checks to validate the integrity and authenticity of the component’s firmware and/or software prior to the boot process, to ensure that the component does not boot into an insecure or invalid operating state that could damage the com ponent or provide a path for a malicious actor to gain access to additional components, assets, or data. | The requirements for the four SL levels that relate to HDR 3.14 are: • SL-C(SI, component) 1: HDR 3.14 • SL-C(SI, component) 2: HDR 3.14 (1) • SL-C(SI, component) 3: HDR 3.14 (1) • SL-C(SI, component) 4: HDR 3.14 (1) 15 Network device requirements 15.1 Purpose The purpose of this set of requirements is to document requirements that are specific to network devices. 15.2 ND R 1.6 – Wireless access management 15.2.1 Requirement A network device supporting wireless access management shall provide the capability to identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. 15.2.2 Rationale and supplemental guidance Any wireless technology can, and in most cases should, be considered as just another communication protocol option. T hus, it should be subject to the same IACS security requirements as any other communication type utilized by the IACS. However, from a security point of view, there is at least one significant difference between wi red and wireless communications. Physical security counterm easures are typically less effective when using wireless. 15.2.3 Requirement enhancements (1) Unique identification and authentication The network device shall provide the capability to uniquely identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. 15.2.4 Security levels The requirements for the four SL levels that relate to ND R 1.6 are: • SL-C(UC, component) 1: ND R 1.6 • SL-C(UC, component) 2: ND R 1.6 (1) • SL-C(UC, component) 3: ND R 1.6 (1) • SL-C(UC, component) 4: ND R 1.6 (1) 15.3 ND R 1.13 – Access via untrusted networks 15.3.1 Requirement The network device supporting device access into a network shall provide the capability to monitor and control all methods of access to the network device via untrusted networks. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 15.3.2 Rationale and supplemental guidance The network device should protect against unauthorized connections or subversion of authorized connections. Examples of access to the network device via untrusted networks typically include remote access methods (such as, dial -up, broadband and wireless) as well as connections from a company’s office (non- control system) network. The network device may provide ACL (access control list) functionality to restrict access by: Layer 2 forwarding devices such as Ethernet swi tches: a) MAC address b) VLAN Layer 3 forwarding devices such as routers, gateways and firewalls: a) IP address b) port and protocol c) virtual private networks 15.3.3 Requirement enhancements (1) Explicit access request approval The network device shall provide the capability to deny access requests via untrusted networks unless explicitly approved by an assigned role. 15.3.4 Security levels The requirements for the four SL levels that relate to ND R 1.13 are: • SL-C(UC, component) 1: ND R 1.13 • SL-C(UC, component) 2: ND R 1.13 • SL-C(UC, component) 3: ND R 1.13 (1) • SL-C(UC, component) 4: ND R 1.13 (1) 15.4 ND R 2.4 – Mobile code 15.4.1 Requirement In the event that a network device utilizes mobile code technologies, the network device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the network device: a) control execution of mobile code; b) control which users (human, software process, or device) are allowed to transfer mobile code to/from the network device; and c) control the code execution based upon integrity checks on mobile code and prior to the code being executed 15.4.2 Rationale and supplemental guidance Mobile c ode technologies include, but are not limited to, Java, JavaScript, ActiveX, PDF, Postscript, Shockwave movies, Flash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and executed on individual workstations. Control procedures should prevent the development, acquisition or introduction of unacceptable mobile code within the control system in which the component resides. For example, mobile code exchanges may be disallowed directly with in © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. Mobile code could be secured by adding integrity, authenticity, and authorization checks to the code itself (application layer), or for “just -in-time” code execution through transmitting the mobile code via a secure communications tunnel which provides these attributes, or any mechanism equivalent to these options. 15.4.3 Requirement enhancements (1) Mobile code authenticity check The network device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. 15.4.4 Security levels The requirements for the four SL levels that relate to NDR 2.4 are: • SL-C(UC, component) 1: ND R 2.4 • SL-C(UC, component) 2: NDR 2.4 (1) • SL-C(UC, component) 3: NDR 2.4 (1) • SL-C(UC, component) 4: NDR 2.4 (1) | [6 empty] | No corresponding SR
99 | 2 | Base requirement | NDR2.13 | NDR 2.13 | NDR | Use of physical diagnostic and test interfaces | Network devices shall protect against unauthorized use of the physical factory diagnostic and test interface(s) (e.g. JTAG debugging). | Factory diagnostic and test interface(s) are created at various locations within the component to assist the component’s developers and factory personnel as they test the functional implementation, and when errors are discovered to subsequently remove them from the component. However, these same interfaces should be carefully protected from access by unauthorized entities to protect the essential functionality provided by the component to the IACS. There may be cases where the factory diagnostic and test interface(s) use network communications with the device. When this is the case those interfaces are to be subjected to all of the requirements of this document. Note that if a diagnostic and te st interface does not provide the ability to control the product, or to access non- public information, then it will not need an authentication mechanism. This should be determined via a threat assessment. An example of this would be JTAG debugging, in which JTAG is used to take control of the processor and execute arbitrary commands, versus a JTAG boundary scan where JTAG is used to simply read information (which may be publicly available information). | The requirements for the four SL levels that relate to NDR 2.13 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: NDR 2.13 • SL-C(SI, component) 3: NDR 2.13 (1) • SL-C(SI, component) 4: NDR 2.13 (1) | [6 empty] | No corresponding SR
100 | 2 | Enhancement | NDR2.13.1 | NDR 2.13 RE (1) | NDR | Active monitoring | Network devices shall provide active monitoring of the device’s diagnostic and test interface(s) and generate an audit log entry when attempts to access these interface(s) are detected. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | Factory diagnostic and test interface(s) are created at various locations within the component to assist the component’s developers and factory personnel as they test the functional implementation, and when errors are discovered to subsequently remove them from the component. However, these same interfaces should be carefully protected from access by unauthorized entities to protect the essential functionality provided by the component to the IACS. There may be cases where the factory diagnostic and test interface(s) use network communications with the device. When this is the case those interfaces are to be subjected to all of the requirements of this document. Note that if a diagnostic and te st interface does not provide the ability to control the product, or to access non- public information, then it will not need an authentication mechanism. This should be determined via a threat assessment. An example of this would be JTAG debugging, in which JTAG is used to take control of the processor and execute arbitrary commands, versus a JTAG boundary scan where JTAG is used to simply read information (which may be publicly available information). | The requirements for the four SL levels that relate to NDR 2.13 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: NDR 2.13 • SL-C(SI, component) 3: NDR 2.13 (1) • SL-C(SI, component) 4: NDR 2.13 (1) | [6 empty] | No corresponding SR
101 | 3 | Base requirement | NDR3.2 | NDR 3.2 | NDR | Protection from malicious code | The network device shall provide for protection from malicious code. | and supplemental guidan ce If a network device is able to uti lize a compensating control, it need not directly support protection from malicious code. One such possible compensating control would be the use of network packet filtering devices to identify and remove malicious code while in transit. It is assumed that the IACS will be responsible for providing the required safeguards. However, for scenarios such as having a local USB host access, the need for protection from malicious code should be evaluated. 15.6.3 Requirem ent enhancements None | The requirements for the four SL levels that relate to ND R 3.2 are: • SL-C(SI, component) 1: NDR 3.2 • SL-C(SI, component) 2: NDR 3.2 • SL-C(SI, component) 3: NDR 3.2 • SL-C(SI, component) 4: NDR 3.2 | SR3.2 | SR 3.2 | Malicious code protection | The control system shall provide the capability to employ protection mechanisms to prevent, detect, report and mitigate the effects of malicious code or unauthorized software. The control system shall provide the capability to update the protection mechanisms. | The control system should us e protection mechanisms to prevent, detect, mitigate and report instances of detected malicious code (for example, viruses, worms, Trojan horses and spyware) transported by electronic mail, electronic mail attachments, Internet access, removable media (for example, universal serial bus (USB) devic es, diskettes or compact disks), PDF documents, web services, network connections and infected laptops or other common means. Detection mechanisms should be able to detect integrity violations of application binari es and data files. Techniques may include, but are not limited to, binary integrity and attributes monitoring, hashing and signature techniques. Mitigation techniques may include, but are not limited to, file cleaning, quarantining, file deletion, host communication restriction and IPSs. Prevention techniques may include, but are not limited to, application blacklisting and whitelisting techniques, removable media control, sandbox techniques and specific computing platforms mechanisms such as restricted firmware update capabilities, No Execute (NX) bit, data execution prevention (DEP), address space layout randomization (ASLR), stack corruption detection and mandatory access controls. See 10.4, SR 6.2 – Continuous monitoring for an associated requirement involving control system monitoring tools and techniques. Prevention and mitigation mechanisms may include those designed for host elements (such as computers and servers) and network -based mechanisms (such as IDS s and IPS s) and those mechanisms focused on control system specific components (such as PLCs and HMIs). | The requirements for the four SL levels that relate to SR 3.2 – Malicious code protectio n are: • SL-C(SI, control system) 1: SR 3.2 • SL-C(SI, control system) 2: SR 3.2 (1) • SL-C(SI, control system) 3: SR 3.2 (1) (2) • SL-C(SI, control system) 4: SR 3.2 (1) (2) | Same base identifier and enhancement sequence
102 | 3 | Base requirement | NDR3.10 | NDR 3.10 | NDR | Support for updates | Network devices shall support the ability to be updated and upgraded. | Network devices over their installed lifetime may require installation of updates and upgrades. There will be cases where network devices are supporting or executing essential functions as well. When this is the case the network device should have mechanisms in place to support patching and updating without impacting the essential functions of high availability systems (see 4.2). One example for providing this capability would be to support redundancy within the network device. | The requirements for the four SL levels that relate to NDR 3.10 are: • SL-C(SI, component) 1: NDR 3.10 • SL-C(SI, component) 2: NDR 3.10 (1) • SL-C(SI, component) 3: NDR 3.10 (1) • SL-C(SI, component) 4: NDR 3.10 (1) | [6 empty] | No corresponding SR
103 | 3 | Enhancement | NDR3.10.1 | NDR 3.10 RE (1) | NDR | Update authenticity and integrity | Network devices shall validate the authenticity and integrity of any software update or upgrade prior to installation. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | Network devices over their installed lifetime may require installation of updates and upgrades. There will be cases where network devices are supporting or executing essential functions as well. When this is the case the network device should have mechanisms in place to support patching and updating without impacting the essential functions of high availability systems (see 4.2). One example for providing this capability would be to support redundancy within the network device. | The requirements for the four SL levels that relate to NDR 3.10 are: • SL-C(SI, component) 1: NDR 3.10 • SL-C(SI, component) 2: NDR 3.10 (1) • SL-C(SI, component) 3: NDR 3.10 (1) • SL-C(SI, component) 4: NDR 3.10 (1) | [6 empty] | No corresponding SR
104 | 3 | Base requirement | NDR3.11 | NDR 3.11 | NDR | Physical tamper resistance and detection | Network devices shall provide tamper resistance and detection mechanisms to protect aga inst unauthorized physical access into the device. | The purpose of tamper resistance mechanisms is to prevent an attempt by an attacker to execute an unauthorized physical action against an IACS device. Secondary to prevention, detection and response are essential should a tampering event occur. Tamper resistance mechanisms are most effectively used in combinations to prevent access to any critical components. Tamper resistance consists of using specialized materials to ma ke tampering of a device or module difficult. This can include such features as hardened enclosures, locks, encapsulation, or security screws. Putting in place tight airflow paths will increase the difficulty of probing the product inter nals. The purpose o f tamper evidence is to ensure that visible or electronic evidence remains when a tampering event occurs. Many simple evidence techniques are comprised of seals and tapes to make it obvious that there has been physical tampering. More sophisticated techniq ues include switches. | The requirements for the four SL levels that relate to NDR 3.11 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: NDR 3.11 • SL-C(SI, component) 3: NDR 3.11 (1) • SL-C(SI, component) 4: NDR 3.11 (1) | [6 empty] | No corresponding SR
105 | 3 | Enhancement | NDR3.11.1 | NDR 3.11 RE (1) | NDR | Notification of a tampering attempt | Network devices shall be capable of automatically providing notification to a configurable set of recipients upon discovery of an attempt to make an unauthorized physica l access. All notifications of tampering shall be logged as part of the overall audit logging function. | The purpose of tamper resistance mechanisms is to prevent an attempt by an attacker to execute an unauthorized physical action against an IACS device. Secondary to prevention, detection and response are essential should a tampering event occur. Tamper resistance mechanisms are most effectively used in combinations to prevent access to any critical components. Tamper resistance consists of using specialized materials to ma ke tampering of a device or module difficult. This can include such features as hardened enclosures, locks, encapsulation, or security screws. Putting in place tight airflow paths will increase the difficulty of probing the product inter nals. The purpose o f tamper evidence is to ensure that visible or electronic evidence remains when a tampering event occurs. Many simple evidence techniques are comprised of seals and tapes to make it obvious that there has been physical tampering. More sophisticated techniq ues include switches. | The requirements for the four SL levels that relate to NDR 3.11 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: NDR 3.11 • SL-C(SI, component) 3: NDR 3.11 (1) • SL-C(SI, component) 4: NDR 3.11 (1) | [6 empty] | No corresponding SR
106 | 3 | Base requirement | NDR3.12 | NDR 3.12 | NDR | Provisioning product supplier roots of trust | Network devices shall provide the capability to provision and protect the confidentiality, integrity, and authenticity of product supplier keys and data to be used as one or more “roots of trust” at the time of manufacture of the device. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | In order for a component to be able to validate the authenticity and integrity of the h ardware, software, and data provided by the product supplier, it should possess a trusted source of data to perform the validation process. This trusted source of data is referred to as the “root of trust” for the system. This trusted source of data may be a set of cryptographic hashes of “known good” software, or it may be the public portion of an asymmetric cryptographic key pair to be used in the validation of cryptographic signatures. This trusted data is often used to validate critical software, firmwa re, and data prior to booting the firmware or operating system of a component, in order to validate that the component will boot into a “known good” state in which all security mechanisms are known to be operational and uncompromised. “Root of trust” data is often protected by software or hardware implemented mechanisms to prevent any modification of the data during normal operations of the component. Modification of product supplier root of trust data is typically limited to the product supplier’s provisioning process, where the product supplier has a trusted process to perform the provisioning of the data. Instead, information to be validated against the root of trust is submitted to the validation process through a hardware or software API which performs the validation and returns the results without exposing the protected data. | The requirements for the four SL levels that relate to NDR 3.12 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: NDR 3.12 • SL-C(SI, component) 3: NDR 3.12 • SL-C(SI, component) 4: NDR 3.12 | [6 empty] | No corresponding SR
107 | 3 | Base requirement | NDR3.13 | NDR 3.13 | NDR | Provisioning asset owner roots of trust | Network devices shall a) provide the capability to provision and protect the confidentiality, integrity, and authenticity of asset owner keys and data to be used as “roots of trust”; and b) support the capability to provision without reliance on components that may be outside of the device’s security zone. | Product suppliers have established mechanisms to ensure that the software and firmware on their components is authentic, and the integrity of that software and firmware has not been compromised. This allows the product supplier to provide the asset owner with a “known good” state from which to operate. However, many product suppliers also provide mechanisms for asset owners to extend the functionality of their devices through the use of mobile code, user programs, or other such means. In order to protect the security of the component, it is important that these extensions to the component’s functionality also be validated to ensure that they are authorized, and that the asset owner has approved of their origins. In order to perform these validations, the component should contain data that provides a way to differentiate between valid and invalid origins. The list of valid and invalid origins will differ from asset owner to asset owner, and it is unlikely that a product supplier will have a complete list of every possible valid origin at time of manufacture. Therefore, it is important that the product supplier provide a way for the asset owner to securely provision their own “roots of © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 trust” which pr ovide the ability to distinguish between origins allowed by the asset owner’s security policy, and those that are not. The authenticity and integrity of these “roots of trust” should be protected so that malicious actors cannot add additional roots of trus t that grant them the ability to operate on the component. Requirements such as NDR 2.4 – Mobile code (15.4) require the component to complete authenticity checks on mobile code prior to the execution of mobile code. The roots of trust provided by this requirement provide the data necessary to validate the origin and integrity of mobile code, allowing the component to independently determine if the code is allowed to execute. A root of trust is used to provide communications security, such as communications integrity required by CR 3.1 – Communication integrity (7.3) or communications confidentiality required by CR 4.1 – Information confidentiality (8.3). | The requirements for the four SL l evels that relate to NDR 3.13 are: • SL-C(SI, component) 1: Not s elected • SL-C(SI, component) 2: NDR 3.13 • SL-C(SI, component) 3: NDR 3.13 • SL-C(SI, component) 4: NDR 3.13 | [6 empty] | No corresponding SR
108 | 3 | Base requirement | NDR3.14 | NDR 3.14 | NDR | Integrity of the boot process | Network devices shall verify the integrity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. | In order to make assurances to an asset owner tha t a component’s security functionality has not been compromised, it is necessary to ensure that the component’s software and firmware has not been tampered with, and that the software and firmware is valid to execute on the component. Therefore, the compon ent should perform checks to validate the integrity and authenticity of the component’s firmware and/or software prior to the boot process, to ensure that the component does not boot into an insecure or invalid operating state that could damage the compone nt or provide a path for a malicious actor to gain access to additional components, assets, or data. | The requirements for the four SL levels that relate to NDR 3.14 are: • SL-C(SI, component) 1: NDR 3.14 • SL-C(SI, component) 2: NDR 3.14 (1) • SL-C(SI, component) 3: NDR 3.14 (1) • SL-C(SI, component) 4: NDR 3.14 (1) | [6 empty] | No corresponding SR
109 | 3 | Enhancement | NDR3.14.1 | NDR 3.14 RE (1) | NDR | Authenticity of the boot process | Network devices shall use the component’s product supplier roots of trust to verity the authenticity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | In order to make assurances to an asset owner tha t a component’s security functionality has not been compromised, it is necessary to ensure that the component’s software and firmware has not been tampered with, and that the software and firmware is valid to execute on the component. Therefore, the compon ent should perform checks to validate the integrity and authenticity of the component’s firmware and/or software prior to the boot process, to ensure that the component does not boot into an insecure or invalid operating state that could damage the compone nt or provide a path for a malicious actor to gain access to additional components, assets, or data. | The requirements for the four SL levels that relate to NDR 3.14 are: • SL-C(SI, component) 1: NDR 3.14 • SL-C(SI, component) 2: NDR 3.14 (1) • SL-C(SI, component) 3: NDR 3.14 (1) • SL-C(SI, component) 4: NDR 3.14 (1) | [6 empty] | No corresponding SR
110 | 5 | Base requirement | NDR5.2 | NDR 5.2 | NDR | Zone boundary protection | A network device at a zone boundary shall provide the capability to monitor and control communications at zone boundaries to enforce the compartmentalization defined in the risk - based zones and conduits model. | Any connections to outside of each security zone should occur through managed interfaces consistin g of appropriate boundary protection devices (for example, proxies, gateways, routers, firewalls, unidirectional gateways, guards and encrypted tunnels) arranged in an effective architecture (for example, firewalls protecting application gateways residing in a DMZ). Control system boundary protections at any designated alternate processing sites should provide the same levels of protection as that of the primary site. | The requirements for the four S L levels that relate to N DR 5.2 are: • SL-C(SI, component) 1: N DR 5.2 • SL-C(SI, component) 2: N DR 5.2 (1) • SL-C(SI, component) 3: N DR 5.2 (1) (2) (3) • SL-C(SI, component) 4: N DR 5.2 (1) (2) (3) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | [6 empty] | No corresponding SR
111 | 5 | Enhancement | NDR5.2.1 | NDR 5.2 RE (1) | NDR | Deny all, permit by exception | The network component shall provide the capability to deny network traffic by default and allow network traffic by exception (also termed deny all, permit by exception). | Any connections to outside of each security zone should occur through managed interfaces consistin g of appropriate boundary protection devices (for example, proxies, gateways, routers, firewalls, unidirectional gateways, guards and encrypted tunnels) arranged in an effective architecture (for example, firewalls protecting application gateways residing in a DMZ). Control system boundary protections at any designated alternate processing sites should provide the same levels of protection as that of the primary site. | The requirements for the four S L levels that relate to N DR 5.2 are: • SL-C(SI, component) 1: N DR 5.2 • SL-C(SI, component) 2: N DR 5.2 (1) • SL-C(SI, component) 3: N DR 5.2 (1) (2) (3) • SL-C(SI, component) 4: N DR 5.2 (1) (2) (3) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | [6 empty] | No corresponding SR
112 | 5 | Enhancement | NDR5.2.2 | NDR 5.2 RE (2) | NDR | Island mode | The network component shall provide the capability to protect against any communication through the control system boundary (also termed island mode). NOTE 1 Examples of when this capability can be used include where a security violation and/or breach has been detected within the control system, or an attack is occurring at the enterprise level. | Any connections to outside of each security zone should occur through managed interfaces consistin g of appropriate boundary protection devices (for example, proxies, gateways, routers, firewalls, unidirectional gateways, guards and encrypted tunnels) arranged in an effective architecture (for example, firewalls protecting application gateways residing in a DMZ). Control system boundary protections at any designated alternate processing sites should provide the same levels of protection as that of the primary site. | The requirements for the four S L levels that relate to N DR 5.2 are: • SL-C(SI, component) 1: N DR 5.2 • SL-C(SI, component) 2: N DR 5.2 (1) • SL-C(SI, component) 3: N DR 5.2 (1) (2) (3) • SL-C(SI, component) 4: N DR 5.2 (1) (2) (3) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | [6 empty] | No corresponding SR
113 | 5 | Enhancement | NDR5.2.3 | NDR 5.2 RE (3) | NDR | Fail close | The network component shall provide the capability to protect against any communication through the control system boundary when there is an operational failure of the boundary protection mechanisms (also termed fail close). NOTE 2 Examples of when this capability can be used include scenarios where a hardware failure or power failure causes boundary protection devices to function in a degraded mode or fail entirely. | Any connections to outside of each security zone should occur through managed interfaces consistin g of appropriate boundary protection devices (for example, proxies, gateways, routers, firewalls, unidirectional gateways, guards and encrypted tunnels) arranged in an effective architecture (for example, firewalls protecting application gateways residing in a DMZ). Control system boundary protections at any designated alternate processing sites should provide the same levels of protection as that of the primary site. | The requirements for the four S L levels that relate to N DR 5.2 are: • SL-C(SI, component) 1: N DR 5.2 • SL-C(SI, component) 2: N DR 5.2 (1) • SL-C(SI, component) 3: N DR 5.2 (1) (2) (3) • SL-C(SI, component) 4: N DR 5.2 (1) (2) (3) © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | [6 empty] | No corresponding SR
114 | 5 | Base requirement | NDR5.3 | NDR 5.3 | NDR | General purpose, person -to-person communication restrictions | A network device at a zone boundary shall provide the capability to protect against general purpose, person- to-person messages from being received from users or systems external to the control system. | General purpose, person -to-person communications systems include but are not limited to: email systems, forms of social media (Twitter, Facebook, picture galleries, etc.) or any message systems that permit the transmission of any type of executable file. These systems are usually utilized for private purposes that are not related to control system operations, and therefore the risks imposed by these systems normally outweigh any perceived benefit. These types of general purpose communications systems are commonly used as attack vectors to introduce malware to the control system, pass information for which read authorization exists to locations external to the control system and introduce excessive network loading that can be used to create security problems or launch attacks on the control system. Network devices could realize such restrictions, for example, by blocking specific communications based on port numbers and source and/or target address as well as more in depth checks by application layer firewalls. | The requirements for the four S L levels that relate to N DR 5.3 are: • SL-C(SI, component) 1: N DR 5.3 • SL-C(SI, component) 2: N DR 5.3 • SL-C(SI, component) 3: N DR 5.3 • SL-C(SI, component) 4: N DR 5.3 © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 Annex A (informative) Device cat egories A.1 General The devices described in these categories are intended as representative samples for each category, and not an exhaustive list. A.2 Device category: embedded device A.2.1 Programmable logic controller (PLC) The term "programmable logic controller" is expanded from IEC 60050 -351:2013, 351 -47-22 [11] and is commonly used in the process and discrete manufacturing industries. A PLC is a device that typically resides on the lower levels of the automation system (such as level 1 and 2 of the Purdue Enterprise Reference Architecture in ANSI/ISA -95.00.01 [15]). PLCs commonly use ruggedized hardware to allow for operation in industrial environments and are commonly based on commercial real-time operating systems (RTOS). Increasingly smart sensor s and actuators are also receiving forms of process control capability. PLCs and smart sensor/actuators are programmed to execute control logic based on inputs from the process (obtained from instrumentation like traditional temperature sensors, pressure sensors, vibration sensors). The control logic's output is used to control the industrial process (through actuators such as valves, pumps). The programming is usuall y done using engineering software commonly run on host devices (for example, laptops or PC workstations). A c ommon programming language for control logic is IEC 61131 -3, [13]. In larger systems, PLCs often also communicate the process conditions as obtained from sensors to higher -level servers and/ or operator workstations and receive instructions from higher -level control functions or operator workstations, which are translated into or forwarded as commands to actuators. For the communication to higher -level functions such as control servers or operator worksta tions, modern PLCs use Ethernet and transmission control protocol (TCP)/Internet protocol (IP)- based protocols, while for the communication to the instrumentation, industry standard fieldbuses are commonly used (some of which are also available on Ethernet carriers, but usually do not use the TCP/IP stack). Special PLCs are used for executi ng safety functions which ensure that the process under control remains within the bounds of safe operation at all times. PLCs, especially executing safety functions, should meet hard real -time and high integrity and availability requirements. A.2.2 Intelligent electronic device (IED) The term "intelligent electronic device" is expanded from IEC TR 61850 -1:2013 [14]. An intelligent electronic device (IED) is conceptually very similar to a PLC, but the term is more commonly used in power systems (specifically substation automation). An IED receives measurements from the power equipment (for example, transformers, switches and circuit breakers) and executes control logic or protection functions. Similar to PLCs, IEDs are commonly programmed and parameterized using engineering software commonly run on host devices (for example laptops and PC workstations). A modern standard way of describing the configuration of IEDs and their functions is defined in IEC TR 61850 -1. The output of the logic executed by IEDs is transmitted to actuators (switches, circuit breakers, etc.). As opposed to PLCs, IEDs commonly also have a HMI which allows a human user standing in front of the IED to use the IED's functionality (often a subset necessary to support essential functions). Also, substations, and therefore the IEDs used therein, have to be able to operate in complete isolation (such as without any communication to higher -level systems outside the substation or even without any communication to other IEDs or station -level workstations or servers). Modern IEDs usually use Ethernet and TCP/IP -based protocols to communicate to higher - level components, while communication to other IEDs may be done using Ethernet -based protocols (in some cases TCP/IP -based, often directly on Ethernet) or fieldbuses (some of © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 which are available also on Ethernet carriers, but do not use the TCP/IP stack). Sim ilar to PLCs, IEDs should meet hard real -time and high integrity and availability requirements. A.3 Device category: network device A.3.1 Switch The term "switch" is expanded from IEC 60050 -732:2010, 732- 01-22 [12]. A switch is a device in computer networks that links multiple network segments or network nodes together. A switch is typically located at layer 2 (data link layer) of the OSI model (see ISO/IEC 7498 -1 [6]). Modern switches, especially those designed for use in larger networks, typical ly provide interfaces for configuration management and network management. These interfaces may support the configuration of the switch (for example web-based via HTTP/HTTPS, file -based via FTP/SFTP, command- line-based via SSH or via simple network management protocol (SNMP)) as well as log and event management (for example via syslog). A.3.2 Virtual private network (VPN) terminator The term "virtual private network" is expanded from IEC 60050 -732:2010, 732 -01-10 [12]. Virtual private networks are logical networks that allow for the extension of private networks across distances that are bridged by public networks. The use of the public network to co ver the distance is transparent/invisible to the VPN users. VPNs are established by creating a logical tunnel at the border of the two segments of the private network. The tunnel is established by VPN terminators, which are devices located at the network border. The data packets from one segment are encapsulated (commonly also encrypted) at the VPN terminator at then sent through a public network to the peer VPN terminator. There, the encapsulation is removed (usually involving decr yption) and the original packet is recovered and forwarded into the local network segment. VPNs are also often used to allow roaming users secure access to resources on their home network. In this scenario, a client software on the roaming device acts as a local VPN terminator, encapsulating (and usually encr ypting) all data packets and forwarding them to the VPN terminator on the home network border. Establishment of the tunnel between VPN terminators should be authenticated, which, in the scenario of roaming users, typically is a user -based authentication. Hence, VPN terminators may be used to collect data about roaming users, which may allow tracing their location and other privacy related data. A.4 Device category: host device/application A.4.1 Operator workstation Operator workstations are used in control systems to display proc ess information to human users or operators and to allow them to interact with the control system (for example initiate operational actions on the process, such as opening a valve, closing a switch, modifying process set poin ts). Depending on the respective operational requirements, operator workstations are often required to be continuously available (at least a minimum set of workstations out of all installed ones) to allow for an uninterrupted view of the process conditions and the opportunity to interact with the process immediately, if necessary. In order to obtain the data to be displayed and to send the commands issued by the human user, operator workstations typically communicate with control servers and connectivity servers in the control systems, sometimes they also directly communicate with PLCs. This communica tion is commonly using Ethernet and TCP/IP -based protocols. Operator workstations typically do not have to meet hard -real time requirements, but have high integ rity and (at least as a set of operator workstations) high availability requirements. They are typically built from COTS PC hardware and run COTS client operating systems. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 A.4.2 Data historian Data historians are used in control systems to collect and maintain long -term process history data. This data is commonly collected from control servers or directly from PLCs using protocols based on Ethernet and TCP/IP. The data may be used in a variety o f analyses, for example, for process optimization or performance reporting but may also be used in reporting to regulatory entities such as emission reporting or documentation of the product's production process integrity (for example, as required by the U S Food and Drug Administration (FDA) regulations for pharmaceutical products). They are typically built from COTS PC/server hardware and run COTS client/server operating systems. Data is commonly stored using COTS database products. Communication to data access clients and data sources is commonly using TCP/IP -based protocols. Depending on the criticality of the process history from a business perspective, data historians have moderate availability and integrity requirements and typically no hard real -time requirements. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 Annex B (informative) Mapping of CRs and REs to FR SL s 1-4 B.1 Overview Annex B is intended to provide overall guidance to the reader as to how SL levels 0 to 4 are differentiated on an FR -by-FR basis via the defined C Rs and their associated REs. B.2 SL mapping table Table B. 1 indicates which component level requirements apply to which FRs for a given component security level capability SL – SL-C(xx, component). For a given FR, the required component level requirem ents to meet a given SL- C are denoted by a check mark. As an example, a component that achieve s SL-1 in FR 7 satisf ies the base requirements of CRs 7.1 through 7.7. Note that satisfying CR 7.8 is not necessary to meet SL -1 because it is not selected until SL-2 and higher security levels. Meeting SL- 1 in this way is also denoted SL-C(RA, component) = 1, to indicate that the component has a capability security level of 1 in resource availability, or FR 7. A component that meet s SL-2 in FR 7, or SL -C(RA, compo nent) = 2 satisf ies all requirements from SL -1, and additionally satisfy CR 7.1 RE(1), CR 7.3 RE(1), and the base requirement for CR 7.8. Similarly, a component that meet s SL-3 in FR 7, or SL- C (RA, component) = 3 satisf ies all requirements from SL- 2, and additionally satisfy CR 7.6 RE(1). A component that meet s SL-4 in FR7, or SL -C(RA, component) = 4 satisf ies all requirements from SL-3. There are no base requirements or requirement enhancements in FR 7 that are unique to SL- 4, and thus all components which meet SL- 3 also inherently meet SL- 4. Refer to IEC 62443‑3‑3:2013, Annex A for how a full SL vector that includes all foundational requirements would be denoted. For clarification the acronyms used in the table are shown at the end of the table. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 Table B. 1 – Mapping of CRs and REs to FR SL levels 1 -4 SRs and R Es SL 1 SL 2 SL 3 SL 4 FR 1 – Identification and authentication control (IAC) CR 1.1 – Human user identification and authentication     RE (1) Unique identification and authentication:    RE (2) Multifactor authentication for all interfaces   CR 1.2 – Software process and device identification and authentication    RE (1) Unique identification and authentication   CR 1.3 – Account management     CR 1.4 – Identifier management     CR 1.5 – Authenticator management     RE (1) Hardware security for authenticators   NDR 1.6 – Wireless access management     RE (1) Unique identification and authentication    CR 1.7 – Strength of password -based authentication     RE (1) Password generation and lifetime restrictions for human users   RE (2) Password lifetime restrictions for all users (human, software process, or device)  CR 1.8 – Public key infrastructure certificates    CR 1.9 – Strength of public key -based authentication    RE (1) Hardware security for public key -based authentication   CR 1.10 – Authenticator feedback     CR 1.11 – Unsuccessful login attempts     CR 1.12 – System use notification     NDR 1.13 – Access via untrusted networks     RE (1) Explicit access request approval   CR 1.14 – Strength of symmetric key -based authentication    RE (1) Hardware security for symmetric key -based authentication   © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 SRs and R Es SL 1 SL 2 SL 3 SL 4 FR 2 – Use control (UC) CR 2.1 – Authorization enforcement     RE (1) Authorization enforcement for all users (humans, software processes and devices)    RE (2) Permission mapping to roles    RE (3) Supervisor override   RE (4) Dual approval  CR 2.2 – Wireless use control     CR 2.3 – Use control for portable and mobile devices SAR 2.4 – Mobile code     RE (1) Mobile code authenticity check    EDR 2.4 – Mobile code     RE (1) Mobile code authenticity check    HDR 2.4 – Mobile code     RE (1) Mobile code authenticity check    NDR 2.4 – Mobile code     RE (1) Mobile code authenticity check    CR 2.5 – Session lock     CR 2.6 – Remote session termination    CR 2.7 – Concurrent session control   CR 2.8 – Audit able events     CR 2.9 – Audit storage capacity     RE (1) Warn when audit record storage capacity threshold reached   CR 2.10 – Response to audit processing failures     CR 2.11 – Timestamps     RE (1) Time synchronization    RE (2) Protection of time source integrity  CR 2.12 – Non-repudiation     RE (1) Non-repudiation for all users  © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 SRs and R Es SL 1 SL 2 SL 3 SL 4 EDR 2.13 – Use of physical diagnostic and test interfaces    RE (1) Active monitoring   HDR 2.13 – Use of physical diagnostic and test interfaces    RE (1) Active monitoring   NDR 2.13 – Use of physical diagnostic and test interfaces    RE (1) Active monitoring   FR 3 – System integrity (SI) CR 3.1 – Communication integrity     RE (1) Communication authentication    SAR 3.2 – Protection from malicious code     EDR 3.2 – Protection from malicious code     HDR 3.2 – Protection from malicious code     RE (1) Report version of code protection    NDR 3.2 – Protection from malicious code     CR 3.3 – Security functionality verification     RE (1) Security functionality verification during normal operation  CR 3.4 – Software and information integrity     RE (1) Authenticity of software and information    RE (2) Automated notification of integrity violations   CR 3.5 – Input validation     CR 3.6 – Deterministic output     CR 3.7 – Error handling     CR 3.8 – Session integrity    CR 3.9 – Protection of audit information    RE (1) Audit records on write -once media  EDR 3.10 – Support for updates     RE (1) Update authenticity and integrity    HDR 3.10 – Support for updates     © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 SRs and R Es SL 1 SL 2 SL 3 SL 4 RE (1) Update authenticity and integrity    NDR 3.10 – Support for updates     RE (1) Update authenticity and integrity    EDR 3.11 – Physical tamper resistance and detection    RE (1) Notification of a tampering attempt   HDR 3.11 – Physical tamper resistance and detection    RE (1) Notification of a tampering attempt   NDR 3.11 – Physical tamper resistance and detection    RE (1) Notification of a tampering attempt   EDR 3.12 – Provisioning product supplier roots of trust    HDR 3.12 – Provisioning product supplier roots of trust    NDR 3.12 – Provisioning product supplier roots of trust    EDR 3.1 3 – Provisioning asset owner roots of trust    HDR 3.13 – Provisioning asset owner roots of trust    NDR 3.13 – Provisioning asset owner roots of trust    EDR 3.14 – Integrity of the boot process     RE (1) Authenticity of the boot process    HDR 3.14 – Integrity of the boot process     RE (1) Authenticity of the boot process    NDR 3.14 – Integrity of the boot process     RE (1) Authenticity of the boot process    FR 4 – Data confidentiality (DC) CR 4.1 – Information confidentiality     CR 4.2 – Information persistence    RE (1) Erase of shared memory resources   RE (2) Erase verification   CR 4.3 – Use of cryptography     © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 SRs and R Es SL 1 SL 2 SL 3 SL 4 FR 5 – Restricted data flow (RDF) CR 5.1 – Network segmentation     NDR 5.2 – Zone boundary protection     RE (1) Deny all, permit by exception    RE (2) Island mode   RE (3) Fail close   NDR 5.3 – General purpose, person -to-person communication restrictions     FR 6 – Timely response to events (TRE) CR 6.1 – Audit log accessibility     RE (1) Programmatic access to audit logs   CR 6.2 – Continuous monitoring    FR 7 – Resource availability (RA) CR 7.1 – Denial of service protection     RE(1) Manage communication load from component    CR 7.2 – Resource management     CR 7.3 – Control system backup     RE (1) Backup integrity verification    CR 7.4 – Control system recovery and reconstitution     CR 7.5 – Emergency power CR 7.6 – Network and security configuration settings     RE (1) Machine -readable reporting of current security settings   CR 7.7 – Least functionality     CR 7.8 – Control system component inventory    Key CR: Component requirement which is common to all types of components SAR: Software application requirement EDR: Embedded device requirement HDR: Host device requirement NDR: Network device requirement © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 Bibliography NOTE 1 This bibliography includes references to sources used in the creation of this document as well as references to sources that can aid the reader in developing a greater understanding of cyber security as a whole and developing a management system. Not all references in this bibliography are referred to throughout the text of this document. The references have been broken down into different categories depending on the type of source they are. References to other parts, both existing and anticipated, of the IEC 62443 series: NOTE 2 Some of these references are published documents, under development, or anticipated. They are all listed here for completeness of the currently authorized parts of the IEC 62443 series. [1] IEC 62443‑2‑1, Industrial communication networks – Network and system security – Part 2- 1: Establishing an industrial automation and control system security program [2] IEC TR 62443‑2‑3, Security for industrial automation and control systems – Part 2-3: Patch management in the IACS environment [3] IEC 62443‑2‑4, Security for industrial automat ion and control systems – Part 2-4: Security program requirements for IACS service providers [4] IEC TR 62443 -3-1, Industrial communication networks – Network and system security – Part 3- 1: Security technologies for industrial automation and control systems [5] IEC 62443 ‑3‑24, Security for industrial automation and control systems – Part 3-2: Security risk assessment and system design Other standards references: [6] ISO/IEC 7498- 1:1994, Information technology – Open Systems Interconnection – Basic Reference Model: The Basic Model [7] ISO/IEC 8601:2004, Data elements and interchange formats – Informati on interchange – Representation of dates and times [8] ISO/IEC 15408 -1:2009, Information technology – Security techniques – Evaluation criteria for IT security – Part 1: Introduction and general model [9] ISO/IEC 19790, Information technology – Security techniques – Security requirements for cryptographic modules [10] ISO/IEC 27002:2013, Information technology – Security techniques – Code of practice for information security management [11] IEC 60050 -351, International Electrotechnical Vocabulary – Part 351: Control technology (available at http://www.electropedia.org) [12] IEC 60050 -732, International Electrotechnical Vocabulary – Part 732: Computer network technology (available at http://www.electropedia.org) [13] IEC 61131 -3, Programmable controllers – Part 3: Programming languages ___________ 4 Under preparation. Stage at the time of publication: IEC PRVC 62443 -3-2:2018. © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 [14] IEC TR 61850 -1:2013, Communication networks and systems for power utility automation – Part 1: Introduction and overview [15] ANSI/ISA -95.00.01 -2010 (IEC 62264 -1 Mod), Enterprise -Control System Integra tion – Part 1: Models and Terminology [16] ISO/IEC 11889 -1:2015, Information technology – Trusted Platform Module Library – Part1: Architecture Other documents and published resources: [17] FIPS 140 -2, Security Requirements for Cryptographic Modules [18] NIST SP 800 -57, Recommendation for Key Management – Part 1: General [19] NIST SP 800 -92, Guide to Computer Security Log Management [20] NIST SP800 -63-2, Electronic Authentication Guideline Websites: [21] OWASP Code Review Guide, available at https://www.owasp.org/index.php/Code_Review_Guide [22] RFC 3647 – Internet X.509 Public Key Infrastructure Certificate Policy and Certification Practices Framework https://www.ietf.org/rfc/rfc3647.txt __________ © Danish Standards FoundationLicensed to: Ole Valente, Kamstrup A/S, 2022-12-05 10:28 | SR5.3 | SR 5.3 | General purpose person -to-person communication restrictions | The control system shall provide the capability to prevent general purpose person -to-person messages from being received from users or systems external to the control system. | General purpose person -to-person communications systems include but are not limited to: email systems, forms of social media (Twitter, Facebook, picture galleries, etc.) or any message systems that permit the transmission of any type of executable file. These systems are usually utilized for private purposes which are not related to control system operations, and therefore the risks imposed by these system s normally outweigh any perceived benefit. These types of general purpose communications systems are commonly used attack vectors to introduce malware to the control system, pass information for which read authorization exists to locations external to the control system, and introduce excessive netw ork loading that can be used to create security problems or launch attacks on the control system. Application of a broad range of other system requirements covering, for example, usage restrictions and limiting data flow as described elsewhere in this standard to general purpose person- to-person communication systems can provide adequate compensating countermeasures to meet this requirement. The control system may provide the capability to utilize these types of two- way communication systems, but only betwe en servers and/or workstations within the control system. Note that this SR needs to support the requirements associated with 8.3, SR 4.1 – Information confidentiality. The control system may also restrict email or other messaging solutions that provide internal computer -to-external computer communications using outbound messages. These internal -toexternal communications may be limited to the purpose of sending system alerts or other computer generated information messages to users or systems external to the control system. To prevent the passing of information for which explicit read authorization is supported, pre - configured messages (perhaps with the ability to include some limited text) should be used to transmit the alerts or status information. Users may not be given the ability to attach files or other information t o these outbound- only messages at the time the messages are created by the system. | The requirements for the four SL levels that relate to SR 5.3 – General purpose person -toperson communication restrictions are: • SL-C(RDF, control system) 1: SR 5.3 • SL-C(RDF, control system) 2: SR 5.3 • SL-C(RDF, control system) 3: SR 5.3 (1) • SL-C(RDF, control system) 4: SR 5.3 (1) | Same base identifier and enhancement sequence

## All SRs
Display ID | Official ID | Row Type | Title | Requirement Text | Rationale and Supplemental Guidance | Security Levels
SR1.1 | SR 1.1 | Base requirement | Human user identification and authentication | The control sys tem shall provide the capability to identify and authenticate all human users. This capability shall enforce such identification and authentication on all interfaces which provide human user access to the control system to support segregation of duties and least privilege in accordance with applicable security polic ies and procedures. | All human users need to be identified and authenticated for all access to the control system. Authentic ation of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or, in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of t he authentication process. This requirement should be applied to both local and remote access to the control system. In addition to identifying and authenticating all human users at the control system level (for example, at system logon), identification a nd authentication mechanisms are often employed at the application level. Where human users function as a single group (such as control room operators), user identification and authentication may be role -based or group- based. For some control system s, the c apability for immediate operator interaction is critical. It is essential that l ocal emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). Access to these systems may be restricted by appropriate physical security mechanisms (see IEC 62443‑2‑1). An example of such a situation is a critical operations room where strict physical access control and monitoring is in place and where shift plans allocate responsibility to a group of users. These users may then be using the same user identity. In addition, the designated operator workstation clients should be authenticated (see 5.4, SR 1.2 – Software process and device identification and authentication) or the use of this shared account should be limited to the constrained environment of the control room. In order to support IAC policies, as defined according to IEC 62443‑2‑1, the control system verif ies the identity of a ll human user s as a first step. In a second step, the permissions assigned to the identified human user are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.1 – Human user identification and authentication are: • SL-C(IAC, control system) 1: SR 1.1 • SL-C(IAC, control system) 2: SR 1.1 (1) • SL-C(IAC, control system) 3: SR 1.1 (1) (2) • SL-C(IAC, control system) 4: SR 1.1 (1) (2) (3)
SR1.1.1 | SR 1.1 RE (1) | Enhancement | Unique identification and authentication | The control system shall provide the capability to uniquely identify and authenticate all human users. | All human users need to be identified and authenticated for all access to the control system. Authentic ation of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or, in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of t he authentication process. This requirement should be applied to both local and remote access to the control system. In addition to identifying and authenticating all human users at the control system level (for example, at system logon), identification a nd authentication mechanisms are often employed at the application level. Where human users function as a single group (such as control room operators), user identification and authentication may be role -based or group- based. For some control system s, the c apability for immediate operator interaction is critical. It is essential that l ocal emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). Access to these systems may be restricted by appropriate physical security mechanisms (see IEC 62443‑2‑1). An example of such a situation is a critical operations room where strict physical access control and monitoring is in place and where shift plans allocate responsibility to a group of users. These users may then be using the same user identity. In addition, the designated operator workstation clients should be authenticated (see 5.4, SR 1.2 – Software process and device identification and authentication) or the use of this shared account should be limited to the constrained environment of the control room. In order to support IAC policies, as defined according to IEC 62443‑2‑1, the control system verif ies the identity of a ll human user s as a first step. In a second step, the permissions assigned to the identified human user are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.1 – Human user identification and authentication are: • SL-C(IAC, control system) 1: SR 1.1 • SL-C(IAC, control system) 2: SR 1.1 (1) • SL-C(IAC, control system) 3: SR 1.1 (1) (2) • SL-C(IAC, control system) 4: SR 1.1 (1) (2) (3)
SR1.1.2 | SR 1.1 RE (2) | Enhancement | Multifactor authentication for untrusted networks | The control system shall provide the capability to employ multifactor authentication for human user access to the control system via an untrusted network (see 5.15, SR 1.13 – Access via untrusted networks). NOTE See 5.7.3. 5.7.3.1, SR 1.5 – Authenticator management, RE 5.7.3.1 for enhanced authenticator management for software processes. | All human users need to be identified and authenticated for all access to the control system. Authentic ation of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or, in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of t he authentication process. This requirement should be applied to both local and remote access to the control system. In addition to identifying and authenticating all human users at the control system level (for example, at system logon), identification a nd authentication mechanisms are often employed at the application level. Where human users function as a single group (such as control room operators), user identification and authentication may be role -based or group- based. For some control system s, the c apability for immediate operator interaction is critical. It is essential that l ocal emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). Access to these systems may be restricted by appropriate physical security mechanisms (see IEC 62443‑2‑1). An example of such a situation is a critical operations room where strict physical access control and monitoring is in place and where shift plans allocate responsibility to a group of users. These users may then be using the same user identity. In addition, the designated operator workstation clients should be authenticated (see 5.4, SR 1.2 – Software process and device identification and authentication) or the use of this shared account should be limited to the constrained environment of the control room. In order to support IAC policies, as defined according to IEC 62443‑2‑1, the control system verif ies the identity of a ll human user s as a first step. In a second step, the permissions assigned to the identified human user are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.1 – Human user identification and authentication are: • SL-C(IAC, control system) 1: SR 1.1 • SL-C(IAC, control system) 2: SR 1.1 (1) • SL-C(IAC, control system) 3: SR 1.1 (1) (2) • SL-C(IAC, control system) 4: SR 1.1 (1) (2) (3)
SR1.1.3 | SR 1.1 RE (3) | Enhancement | Multifactor authentication for all networks | The control system shall provide the capability to employ multifactor authentication for all human user access to the control system. | All human users need to be identified and authenticated for all access to the control system. Authentic ation of the identity of these users should be accomplished by using methods such as passwords, tokens, biometrics or, in the case of multifactor authentication, some combination thereof. The geographic location of human users can also be used as part of t he authentication process. This requirement should be applied to both local and remote access to the control system. In addition to identifying and authenticating all human users at the control system level (for example, at system logon), identification a nd authentication mechanisms are often employed at the application level. Where human users function as a single group (such as control room operators), user identification and authentication may be role -based or group- based. For some control system s, the c apability for immediate operator interaction is critical. It is essential that l ocal emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). Access to these systems may be restricted by appropriate physical security mechanisms (see IEC 62443‑2‑1). An example of such a situation is a critical operations room where strict physical access control and monitoring is in place and where shift plans allocate responsibility to a group of users. These users may then be using the same user identity. In addition, the designated operator workstation clients should be authenticated (see 5.4, SR 1.2 – Software process and device identification and authentication) or the use of this shared account should be limited to the constrained environment of the control room. In order to support IAC policies, as defined according to IEC 62443‑2‑1, the control system verif ies the identity of a ll human user s as a first step. In a second step, the permissions assigned to the identified human user are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.1 – Human user identification and authentication are: • SL-C(IAC, control system) 1: SR 1.1 • SL-C(IAC, control system) 2: SR 1.1 (1) • SL-C(IAC, control system) 3: SR 1.1 (1) (2) • SL-C(IAC, control system) 4: SR 1.1 (1) (2) (3)
SR1.2 | SR 1.2 | Base requirement | Software process and device identification and authentication | The control system shall provide the capability to identify and authenticate all software processes and devices. This capability shall enforce such identification and authentication on all interfaces which provide access to the control system to support least privilege in accordance with applicable security policies and procedures. | The function of identification and authentication is to map an ID to an unknown software process or device (henceforth referred to an entity in this sub- clause) so as to make it known before allowing any data exchange. Allowing rogue entities to send and receive control system specific data can result in detrimental behavior of the legitimate control system. All entities need to be identified and authenticated for all access to the control system. Authentication of the identity of such entities should be accomplished by using methods such as passwords, tokens or location (physical or logical). This requirement should be applied to both local and remote access to the control system. However, in some scenarios where individual entities are used to conn ect to different target systems (for example, remote vendor support), it may be technical ly infeasible for an entity to have multiple identities. In these cases, compensating countermeasures would have to be applied. Identification and authentication mechanisms for all entities are needed to protect against attacks such as man- in-the-middle or message spoofing. In some cases, these mechanism s may involve multiple software processes running on the same physical server, each having their own identity. In other cases, the identity may be bound to the physical device, such as all processes running on a given PLC. Special attention needs to be made when identifying and authenticating portable and mobile devices. These types of devices are a known method of introducing undesired network traffic, malware and/or information exposure to control systems, including otherwise isolated networks. Where entities function as a single group, identification and authentication may be role -based, group -based or entity -based, i t is essential that local emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). For example, in common protection and control schemes, a group of devices jointly execute the protection functions and communicate with multicast messages among the devices in the group. In these cases, group authentication based on shared accounts or shared symmetric keys are commonly used. In order to support identification and authentication control policies as defined according to IEC 62443‑2‑1, the control system verifies the identity of all entities as a first step. In a second step, the permissions assigned to the identified entity are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.2 – Software process and device identification and authentication are: • SL-C(IAC, control system) 1: Not Selected • SL-C(IAC, control system) 2: SR 1.2 • SL-C(IAC, control system) 3: SR 1.2 (1) • SL-C(IAC, control system) 4: SR 1.2 (1)
SR1.2.1 | SR 1.2 RE (1) | Enhancement | Unique identification an d authentication | The control system shall provide the capability to uniquely identify and authenticate all software processes and devices. 5.4.3.2 Void | The function of identification and authentication is to map an ID to an unknown software process or device (henceforth referred to an entity in this sub- clause) so as to make it known before allowing any data exchange. Allowing rogue entities to send and receive control system specific data can result in detrimental behavior of the legitimate control system. All entities need to be identified and authenticated for all access to the control system. Authentication of the identity of such entities should be accomplished by using methods such as passwords, tokens or location (physical or logical). This requirement should be applied to both local and remote access to the control system. However, in some scenarios where individual entities are used to conn ect to different target systems (for example, remote vendor support), it may be technical ly infeasible for an entity to have multiple identities. In these cases, compensating countermeasures would have to be applied. Identification and authentication mechanisms for all entities are needed to protect against attacks such as man- in-the-middle or message spoofing. In some cases, these mechanism s may involve multiple software processes running on the same physical server, each having their own identity. In other cases, the identity may be bound to the physical device, such as all processes running on a given PLC. Special attention needs to be made when identifying and authenticating portable and mobile devices. These types of devices are a known method of introducing undesired network traffic, malware and/or information exposure to control systems, including otherwise isolated networks. Where entities function as a single group, identification and authentication may be role -based, group -based or entity -based, i t is essential that local emergency actions as well as control system essential functions not be hampered by identification or authentication requirements (see Clause 4 for a more complete discussion). For example, in common protection and control schemes, a group of devices jointly execute the protection functions and communicate with multicast messages among the devices in the group. In these cases, group authentication based on shared accounts or shared symmetric keys are commonly used. In order to support identification and authentication control policies as defined according to IEC 62443‑2‑1, the control system verifies the identity of all entities as a first step. In a second step, the permissions assigned to the identified entity are enforced (see 6.3, SR 2.1 – Authorization enforcement). | The requirements for the four SL levels that relate to SR 1.2 – Software process and device identification and authentication are: • SL-C(IAC, control system) 1: Not Selected • SL-C(IAC, control system) 2: SR 1.2 • SL-C(IAC, control system) 3: SR 1.2 (1) • SL-C(IAC, control system) 4: SR 1.2 (1)
SR1.3 | SR 1.3 | Base requirement | Account management | The control system shall provide the capability to support the management of all accounts by authorized users, including adding, a ctivating, modifying, disabling and removing accounts. | Account management may include grouping of accounts (for example, individual, role -based, device -based and control system), establishment of conditions for group membership and assignment of associated authorizations. In certain IACS instances, where individual accounts are determined to be unnecessary from a risk -analysis and/or regulatory aspect, shared accounts are acceptable as long as adequate compensating countermeasures (such as limited physical access or organizational measures for approval) are in place and documented. Non-human user accounts (sometimes termed service accounts) that are utilized for software process -to-process communication (for example, control server to historian and PLC to control server) typic ally require different security policies and procedures from human user accounts. For enhanced security, management of accounts should be done according to unified policies and deployed locally in the relevant components of the control system. Unused default system accounts used for the first installation of the system should be removable. Security enhancement lies in the simplification and consistent application of account management. | The requirements for the four SL levels that relate to SR 1.3 – Account management are: • SL-C(IAC, control system) 1: SR 1. 3 • SL-C(IAC, control system) 2: SR 1. 3 • SL-C(IAC, control system) 3: SR 1. 3 (1) • SL-C(IAC, control system) 4: SR 1. 3 (1)
SR1.3.1 | SR 1.3 RE (1) | Enhancement | Unified account management | The control system shall provide the capability to support unified account management. 5.5.3.2 Void | Account management may include grouping of accounts (for example, individual, role -based, device -based and control system), establishment of conditions for group membership and assignment of associated authorizations. In certain IACS instances, where individual accounts are determined to be unnecessary from a risk -analysis and/or regulatory aspect, shared accounts are acceptable as long as adequate compensating countermeasures (such as limited physical access or organizational measures for approval) are in place and documented. Non-human user accounts (sometimes termed service accounts) that are utilized for software process -to-process communication (for example, control server to historian and PLC to control server) typic ally require different security policies and procedures from human user accounts. For enhanced security, management of accounts should be done according to unified policies and deployed locally in the relevant components of the control system. Unused default system accounts used for the first installation of the system should be removable. Security enhancement lies in the simplification and consistent application of account management. | The requirements for the four SL levels that relate to SR 1.3 – Account management are: • SL-C(IAC, control system) 1: SR 1. 3 • SL-C(IAC, control system) 2: SR 1. 3 • SL-C(IAC, control system) 3: SR 1. 3 (1) • SL-C(IAC, control system) 4: SR 1. 3 (1)
SR1.4 | SR 1.4 | Base requirement | Identifier management | The control system shall provide the capability to support the management of identifiers by user, group, role or control system interface. | Identifiers are distinguished from the privileges which they permit an entity to perform within a specific control system control domain or zone (see 6.3, SR 2.1 – Authori zation enforcement). Where human users function as a single group (such as control room operators), user identification may be role -based, group- based or device- based. For some control sys tems, the capability for immediate operator interaction is critical. Local emergency actions for the control system should not be hampered by identification requirements. Access to these systems may be restricted by appropriate compensating countermeasures. Identifiers may be required on portions of the control system but not necessarily the entire control system. For example, wireless devices typically require identifiers, whereas wired devices may not. The management of identifiers will be determined by local policies and procedures established in compliance with IEC 62443‑2‑1. | The requirements for the four SL levels that relate to SR 1.4 – Identifier management are: • SL-C(IAC, control system) 1: SR 1. 4 • SL-C(IAC, control system) 2: SR 1. 4 • SL-C(IAC, control system) 3: SR 1. 4 • SL-C(IAC, control system) 4: SR 1. 4
SR1.5 | SR 1.5 | Base requirement | Authenticator management | The control system shall provide the capability to: h) initialize authenticator content; i) change all default authenticators upon control system installation; j) change/refresh all authenticators; and k) protect all authenticat ors from unauthorized disclosure and modification when stored and transmitte d. | In addition to an identifier (see 5.6, SR 1.4 – Identifier management) an authenticator is required to prove identity. Control system authenticators include, but are not limited to, tokens, symmetric keys, private keys (part of a public/private key pair), biometrics, passwords, physical keys and key cards. Human users should take reasonable measures to safeguard authenticators, including maintaining possession of their individual authenticators, not loaning or sharing authenticators with others and reporting lost or compromi sed authenticators immediately. Authenticators have a lifecycle. When an account is created automatically a new authenticator needs to be created, in order for the account owner to be able to authenticate. For example, in a password- based system, the account has a password associated with it. Definition of the initial authenticator content could be interpreted as the administrator defining the initial password which the account management system sets for all new accounts. Being able to configure these initial values makes it harder for an attacker to guess the password between account creation and first account use (which should involve t he setting of a new password by the account owner). Some control systems are installed with unattended installers which create all necessary accounts with default passwords and some embedded devices are shipped with default passwords. Over time, these pass words often become general knowledge and are documented on the Internet. Being able to change the default passwords protects the system against unauthorized users using default passwords to gain access. Passwords can be obtained from storage or from transm ission when used in network authentication. The complexity of this can be increased by cryptographic protections such as encryption or hashing or by handshake protocols which do no t require transmission of the password at all. Still, passwords might be subject to attacks, for example brute force guessing or breaking the cryptographic protection of passwords in transit or storage. The window of opportunity can be reduced by changing/refreshing the passwords periodically. Similar considerations apply to authentication systems based on cryptographic keys. Enhanced protection can be achieved by using hardware mechanisms such as hardware security modules like trusted platform modules (TPMs). The management of authenticators should be specified in applicable secur ity policies and procedures, for example, constraints to change default authenticators, refresh periods, specification of the protection of authenticators or firecall (see 3.1.24) procedures. Lockout or loss of control due to security measures is not acceptable. If the control system is required to have a high level of availability, measures should be taken to maintain this high level of availability (such as compensating ph ysical countermeasures, duplicate keys and supervisory override). Besides the capabilities for authenticator management specified in this requirement, the strength of the authentication mechanism depends on the strength of the chosen authenticator (for example password complexity or key length in public key authentication) and the policies for validating the authenticator in the authentication process (for example how long a password is valid or which checks are performed in public key certi ficate validation). For the most common authentication mechanisms password- based and public key authentication 5.9, SR 1.7 – Strength of passw ord-based authentication, 5.10, SR 1.8 – Public key infrastructure (PKI) c ertificates and 5.11, SR 1.9 – Strength of public key authentication provide further requirements. | The requirements for the four SL levels that relate to SR 1.5 – Authenticator management are: • SL-C(IAC, control system) 1: SR 1. 5 • SL-C(IAC, control system) 2: SR 1. 5 • SL-C(IAC, control system) 3: SR 1. 5 (1) • SL-C(IAC, control system) 4: SR 1. 5 (1)
SR1.5.1 | SR 1.5 RE (1) | Enhancement | Hardware security for software process identity credentials | For software process and device users, the control system shall provide the capability to protect the relevant authenticators via hardware mechanisms. 5.7.3.2 Void | In addition to an identifier (see 5.6, SR 1.4 – Identifier management) an authenticator is required to prove identity. Control system authenticators include, but are not limited to, tokens, symmetric keys, private keys (part of a public/private key pair), biometrics, passwords, physical keys and key cards. Human users should take reasonable measures to safeguard authenticators, including maintaining possession of their individual authenticators, not loaning or sharing authenticators with others and reporting lost or compromi sed authenticators immediately. Authenticators have a lifecycle. When an account is created automatically a new authenticator needs to be created, in order for the account owner to be able to authenticate. For example, in a password- based system, the account has a password associated with it. Definition of the initial authenticator content could be interpreted as the administrator defining the initial password which the account management system sets for all new accounts. Being able to configure these initial values makes it harder for an attacker to guess the password between account creation and first account use (which should involve t he setting of a new password by the account owner). Some control systems are installed with unattended installers which create all necessary accounts with default passwords and some embedded devices are shipped with default passwords. Over time, these pass words often become general knowledge and are documented on the Internet. Being able to change the default passwords protects the system against unauthorized users using default passwords to gain access. Passwords can be obtained from storage or from transm ission when used in network authentication. The complexity of this can be increased by cryptographic protections such as encryption or hashing or by handshake protocols which do no t require transmission of the password at all. Still, passwords might be subject to attacks, for example brute force guessing or breaking the cryptographic protection of passwords in transit or storage. The window of opportunity can be reduced by changing/refreshing the passwords periodically. Similar considerations apply to authentication systems based on cryptographic keys. Enhanced protection can be achieved by using hardware mechanisms such as hardware security modules like trusted platform modules (TPMs). The management of authenticators should be specified in applicable secur ity policies and procedures, for example, constraints to change default authenticators, refresh periods, specification of the protection of authenticators or firecall (see 3.1.24) procedures. Lockout or loss of control due to security measures is not acceptable. If the control system is required to have a high level of availability, measures should be taken to maintain this high level of availability (such as compensating ph ysical countermeasures, duplicate keys and supervisory override). Besides the capabilities for authenticator management specified in this requirement, the strength of the authentication mechanism depends on the strength of the chosen authenticator (for example password complexity or key length in public key authentication) and the policies for validating the authenticator in the authentication process (for example how long a password is valid or which checks are performed in public key certi ficate validation). For the most common authentication mechanisms password- based and public key authentication 5.9, SR 1.7 – Strength of passw ord-based authentication, 5.10, SR 1.8 – Public key infrastructure (PKI) c ertificates and 5.11, SR 1.9 – Strength of public key authentication provide further requirements. | The requirements for the four SL levels that relate to SR 1.5 – Authenticator management are: • SL-C(IAC, control system) 1: SR 1. 5 • SL-C(IAC, control system) 2: SR 1. 5 • SL-C(IAC, control system) 3: SR 1. 5 (1) • SL-C(IAC, control system) 4: SR 1. 5 (1)
SR1.6 | SR 1.6 | Base requirement | Wireless access management | The control system shall provide the capability to identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. | Any wireless technology can, and in most cases should, be considered just another communication protocol option, and thus subject to the same IACS security requirements as any other communication type utilized by the IACS. However, from a security point of view, there is at least one significant difference between wired and wireless communications: physical security countermeasures are typically less effective when using wireless. For this and possibly other reasons (for example regulatory differences), a risk analysis might legitimately result in a higher SL-T (IAC,control sy stem) for wireless communications versus a wired protocol being used in an identical use case. Wireless technologies include, but are not limited to, microwave, satellite, packet radio, Institute of Electrical and Electronics Engineers (IEEE) 802.11x, IEEE 802.15.4 (ZigBee, IEC 62591 – Wireless HART®, ISA -100.11a), IEEE 802.15.1 (Bluetooth), wireless LAN mobile routers, mobile phones with tethering and various infrared technologies. | The requirements for the four SL levels that relate to SR 1.6 – Wireless access management are: • SL-C(IAC, control system) 1: SR 1.6 • SL-C(IAC, control system) 2: SR 1.6 (1) • SL-C(IAC, control system) 3: SR 1.6 (1) • SL-C(IA C, control system) 4: SR 1.6 (1)
SR1.6.1 | SR 1.6 RE (1) | Enhancement | Unique identification and authenticat ion | The control system shall provide the capability to uniquely identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. 5.8.3.2 Void | Any wireless technology can, and in most cases should, be considered just another communication protocol option, and thus subject to the same IACS security requirements as any other communication type utilized by the IACS. However, from a security point of view, there is at least one significant difference between wired and wireless communications: physical security countermeasures are typically less effective when using wireless. For this and possibly other reasons (for example regulatory differences), a risk analysis might legitimately result in a higher SL-T (IAC,control sy stem) for wireless communications versus a wired protocol being used in an identical use case. Wireless technologies include, but are not limited to, microwave, satellite, packet radio, Institute of Electrical and Electronics Engineers (IEEE) 802.11x, IEEE 802.15.4 (ZigBee, IEC 62591 – Wireless HART®, ISA -100.11a), IEEE 802.15.1 (Bluetooth), wireless LAN mobile routers, mobile phones with tethering and various infrared technologies. | The requirements for the four SL levels that relate to SR 1.6 – Wireless access management are: • SL-C(IAC, control system) 1: SR 1.6 • SL-C(IAC, control system) 2: SR 1.6 (1) • SL-C(IAC, control system) 3: SR 1.6 (1) • SL-C(IA C, control system) 4: SR 1.6 (1)
SR1.7 | SR 1.7 | Base requirement | Strength of p assword -based authentication | For control systems utilizing password- based authentication, the control system shall provide the capability to enforce configurable password strength based on minimum length and variety of character types. | User authentication based on a username and a secret password is a very commonly used mechanism. Many attacks on such mechanisms focus on guessing the password (for example, dictionary attacks or targeted social engineering) or breaking the cryptographic protection of the stored password representation (for example, using rainbow tables or bruteforcing a hash collision). Increasing the size of the set of valid passwords by incr easing the number of allowed characters makes such attacks more complex, but only if the increased set size is actually used (generally users would tend to not include special characters in a password as they are perceived as harder to remember). Limiting the lifetime of a password decreases the window of opportunity for an attacker to breach a given password’s secrecy. In order to prevent users from circumventing this control by once changing their password to a new one and then immediately changing back t o their original password, a minimum lifetime for a password is commonly enforced as well. A notification to change the password prior the expiration allows the user to change the password at a convenient time according to process operations conditions. This protection can be further enhanced by limiting the reuse of passwords (preventing small sets of alternating passwords), which further decreases the usefulness of a once- breached password. Extended protection beyond password based mechanisms can be ach ieved using multifactor authentication (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication). | The requirements for the four SL levels that relate to SR 1.7 – Strength of password- based authenticati on are: • SL-C(IAC, control system) 1: SR 1. 7 • SL-C(IAC, control system) 2: SR 1. 7 • SL-C(IAC, control system) 3: SR 1. 7 (1) • SL-C(IAC, control system) 4: SR 1. 7 (1) (2)
SR1.7.1 | SR 1.7 RE (1) | Enhancement | Password generation and lifetime restrictions for human users | The control system shall provide the capability to prevent any given human user account from reusing a password for a configurable number of generations. In addition, the control system shall provide the capability to enforce password minimum and maximum lifetime restrictions for human users. These capabilities shall conform with commonly accepted security industry practices. NOTE It is a commonly accepted good practice that the control system provides the capability to prompt the user to change his password upon a configurable time prior to expiration. | User authentication based on a username and a secret password is a very commonly used mechanism. Many attacks on such mechanisms focus on guessing the password (for example, dictionary attacks or targeted social engineering) or breaking the cryptographic protection of the stored password representation (for example, using rainbow tables or bruteforcing a hash collision). Increasing the size of the set of valid passwords by incr easing the number of allowed characters makes such attacks more complex, but only if the increased set size is actually used (generally users would tend to not include special characters in a password as they are perceived as harder to remember). Limiting the lifetime of a password decreases the window of opportunity for an attacker to breach a given password’s secrecy. In order to prevent users from circumventing this control by once changing their password to a new one and then immediately changing back t o their original password, a minimum lifetime for a password is commonly enforced as well. A notification to change the password prior the expiration allows the user to change the password at a convenient time according to process operations conditions. This protection can be further enhanced by limiting the reuse of passwords (preventing small sets of alternating passwords), which further decreases the usefulness of a once- breached password. Extended protection beyond password based mechanisms can be ach ieved using multifactor authentication (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication). | The requirements for the four SL levels that relate to SR 1.7 – Strength of password- based authenticati on are: • SL-C(IAC, control system) 1: SR 1. 7 • SL-C(IAC, control system) 2: SR 1. 7 • SL-C(IAC, control system) 3: SR 1. 7 (1) • SL-C(IAC, control system) 4: SR 1. 7 (1) (2)
SR1.7.2 | SR 1.7 RE (2) | Enhancement | Password lifetime restrictions for all users | The contro l system shall provide the capability to enforce password minimum and maximum lifetime restrictions for all user s. | User authentication based on a username and a secret password is a very commonly used mechanism. Many attacks on such mechanisms focus on guessing the password (for example, dictionary attacks or targeted social engineering) or breaking the cryptographic protection of the stored password representation (for example, using rainbow tables or bruteforcing a hash collision). Increasing the size of the set of valid passwords by incr easing the number of allowed characters makes such attacks more complex, but only if the increased set size is actually used (generally users would tend to not include special characters in a password as they are perceived as harder to remember). Limiting the lifetime of a password decreases the window of opportunity for an attacker to breach a given password’s secrecy. In order to prevent users from circumventing this control by once changing their password to a new one and then immediately changing back t o their original password, a minimum lifetime for a password is commonly enforced as well. A notification to change the password prior the expiration allows the user to change the password at a convenient time according to process operations conditions. This protection can be further enhanced by limiting the reuse of passwords (preventing small sets of alternating passwords), which further decreases the usefulness of a once- breached password. Extended protection beyond password based mechanisms can be ach ieved using multifactor authentication (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication). | The requirements for the four SL levels that relate to SR 1.7 – Strength of password- based authenticati on are: • SL-C(IAC, control system) 1: SR 1. 7 • SL-C(IAC, control system) 2: SR 1. 7 • SL-C(IAC, control system) 3: SR 1. 7 (1) • SL-C(IAC, control system) 4: SR 1. 7 (1) (2)
SR1.9 | SR 1.9 | Base requirement | Strength of public key authentication | For control systems utilizing public key authentication, the control system shall provide the capability to: a) validate certificates by checking the validity of the signature of a given certificate; b) validate certificates by constructing a certification path to an accepted CA or in the case of self-signed certificates by deploying l eaf certificates to all hosts which communicate with the subject to which the certificate is issued; c) validate certificates by checking a given certificate’s revocation status; d) establish user (human, software process or device) control of the corresponding private key; and e) map the authenticated identity to a user (human, software process or device). | Public/private key cryptography strongly depends on the secrecy of a given subject’s private key and proper handling of the trust relationships. When verifying a trust between two entities based on public key authentication, it is essential to trace the public key certificate to a trusted entity. A common implementation error in certificate validation is to only check the validi ty of a certificate’s signature, but not checking the trust in the signer. In a PKI setting, a signer is trusted if they are a trusted CA or have a certificate issued by a trusted CA, thus all verifiers need to trace certificates presented to them back to a trusted CA. If such a chain of trusted CAs canno t be established, the presented certificate should not be trusted. If self -signed certificates are used instead of a PKI, the certificate subject itself signed its certificate, thus there never is a trusted third -party or CA. This should be compensated by deploying the self -signed public key certificates to all peers that need to validate them via an otherwise secured mechanism (for example, configuration of all peers in a trusted environment). Trusted certificates need to be distributed to peers through secure channels. During the validation process, a self -signed certificate should only be trusted if it is already present in the list of trusted certificates of the validating peer. The set of trusted certifi cates should be configured to the minimum necessary set. In both cases, validation needs to also consider the possibility that a certificate is revoked. In a PKI setting this is typically done by maintaining certificate revocation lists (CRLs) or running an online certificate status protocol (OCSP) server. When revocation checking is not available due to control system constraints, mechanisms such as a short certificate lifetime can compensate for the lack of timely revocation information. Note that short lifetime certificates can sometimes create significant operational issues in a control system environment. | The requirements for the four SL levels that relate to SR 1.9 – Strength of public key authentication are: • SL-C(IAC, control system) 1: Not Selected • SL-C(IAC, control system) 2: SR 1. 9 • SL-C(IAC, control system) 3: SR 1. 9 (1) • SL-C(IAC, control system) 4: SR 1. 9 (1)
SR1.9.1 | SR 1.9 RE (1) | Enhancement | Hardware security for public key authentication | The control system shall provide the capability to protect the relevant private keys via hardware mechanisms according to commonly accepted security industry practices and recommendations. 5.11.3.2 Void | Public/private key cryptography strongly depends on the secrecy of a given subject’s private key and proper handling of the trust relationships. When verifying a trust between two entities based on public key authentication, it is essential to trace the public key certificate to a trusted entity. A common implementation error in certificate validation is to only check the validi ty of a certificate’s signature, but not checking the trust in the signer. In a PKI setting, a signer is trusted if they are a trusted CA or have a certificate issued by a trusted CA, thus all verifiers need to trace certificates presented to them back to a trusted CA. If such a chain of trusted CAs canno t be established, the presented certificate should not be trusted. If self -signed certificates are used instead of a PKI, the certificate subject itself signed its certificate, thus there never is a trusted third -party or CA. This should be compensated by deploying the self -signed public key certificates to all peers that need to validate them via an otherwise secured mechanism (for example, configuration of all peers in a trusted environment). Trusted certificates need to be distributed to peers through secure channels. During the validation process, a self -signed certificate should only be trusted if it is already present in the list of trusted certificates of the validating peer. The set of trusted certifi cates should be configured to the minimum necessary set. In both cases, validation needs to also consider the possibility that a certificate is revoked. In a PKI setting this is typically done by maintaining certificate revocation lists (CRLs) or running an online certificate status protocol (OCSP) server. When revocation checking is not available due to control system constraints, mechanisms such as a short certificate lifetime can compensate for the lack of timely revocation information. Note that short lifetime certificates can sometimes create significant operational issues in a control system environment. | The requirements for the four SL levels that relate to SR 1.9 – Strength of public key authentication are: • SL-C(IAC, control system) 1: Not Selected • SL-C(IAC, control system) 2: SR 1. 9 • SL-C(IAC, control system) 3: SR 1. 9 (1) • SL-C(IAC, control system) 4: SR 1. 9 (1)
SR1.10 | SR 1.10 | Base requirement | Authenticator feedback | The control system shall provide the capability to obscure feedback of authentication information during the authentication process. | Obscuring feedback protects the information from possible exploitatio n by unauthorized individuals, f or example, displaying asterisks or other random characters when a human user types in a password obscures feedback of authentication information. Other examples include the entry of wired equivalent priv acy (WEP) keys, secure socket shell (SSH) token entry and RSA one -time passwords. The authenticating entity should not provide any hint as to the reason for the authentication failure, such as “unknown user name”. | The requirements for the four SL levels that relate to SR 1.10 – Authenticator feedback are: • SL-C(IAC, control system) 1: SR 1. 10 • SL-C(IAC, control system) 2: SR 1.10 • SL-C(IAC, control system) 3: SR 1. 10 • SL-C(IAC, control system) 4: SR 1. 10
SR1.11 | SR 1.11 | Base requirement | Unsuccessful login attempts | The control system shall provide the capability to enforce a limit of a configurable number of consecutive invalid access attempts by an y user (human, software process or device) during a configurable time period. The control system shall provide the capability to deny access for a specified period of time or until unlocked by an administrator when this limit has been exceede d. For system accounts on behalf of which critical services or servers are run, the control system shall provide the capability to disallow interactive logons. | Due to the potential for denial of service, the number of consecutive invalid access attempts may be limited. If enabled, the control system may automatically reset to zero the number of access attempts after a predetermined time period established by the applicable security polic ies and procedures. Resetting the access attempts to zero will allow users (human, software process or device) to gain access if they have the correct login identifier. Automatic denial of access for control system operator workstations or nodes should not be used when immediate operator responses are required in emergency situations. All lockout mechanisms should consider functional requirements for continuous operations so as to mitigate adverse denial of service operating conditions which could result in total system f ailure or injury to personnel. Allowing interactive logins to an account used for critical services could provide a potential for denial of service or other abuse. | The requirements for the four SL levels that relate to SR 1.11 – Unsuccessful login attempts are: • SL-C(IAC, control system) 1: SR 1. 11 • SL-C(IAC, control system) 2: SR 1. 11 • SL-C(IAC, control system) 3: SR 1. 11 • SL-C(IAC, control system) 4: SR 1. 11
SR1.12 | SR 1.12 | Base requirement | System use notification | The control system shall provide the capability to display a system use notification message before authenticating. The system use notification message shall be configurable by authorized per sonnel. | Privacy and security policies and procedures need to be consistent with applicable laws, directives, policies, regulat ions, standards and guidance. Often the main justification for this requirement is legal prosecution of violators and proving intentional breach. This capability is thus necessary to support policy requirements, and does not improve IACS security. System use notification messages can be implemented in the form of warning banners displayed when individuals log in to the control system. A warning banner implemented as a posted physical notice in the control system facility does not protect against remote login issues. Examples of elements for inclusion in the system use notification message are: a) that the individual is accessing a specific control system; b) that system usage may be monitored, recorded and subject to audit; c) that unauthorized use of the system is prohibited and subject to criminal and/or civil penalties; and d) that use of the system indicates consent to monitoring and recording. | The requirements for the four SL levels that relate to SR 1.12 – System use notification are: • SL-C(IAC, control system) 1: SR 1. 12 • SL-C(IAC, control system) 2: SR 1. 12 • SL-C(IAC, control system) 3: SR 1. 12 • SL-C(IAC, control system) 4: SR 1. 12 5.15 SR 1.1 3 – Access via untrusted networks Requirement 5.15.1The control system shall provide the capability to monitor and control all methods of access to the control system via untrusted networks. Rationale and supplemental guidance 5.15.2 Examples of access to the control system via untrusted networks typically include remote access methods (such as dial-up, broadband and wireless) as well as connections from a company’s office (non -control system) network. The control system should restrict access achieved through dial -up connections (for example, limiting dial -up access based upon the source of the request) or protect against unauthorized connections or subversion of authorized connections (for example, using virtua l private network technology). Access via untrusted networks to geographically remote control system component locations (for example, control centres and field locations) should only be enabled when necessary and authenticated. Security policies and procedures may require multifactor authentication for remote user access to the control system. Requirement enhancements 5.15.3 5.15.3.1 SR 1.13 RE 1 – Explicit access request approval The control system shall provide the capability to deny access requests via untrusted networks unless approved by an assigned role. 5.15.3.2 Void Security levels 5.15.4 The requirements for the four SL levels that relate to SR 1.13 – Access via untrusted networks are: • SL-C(IAC, control system) 1: SR 1.1 3 • SL-C(IAC, control system) 2: SR 1.1 3 (1) • SL-C(IAC, control system) 3: SR 1.1 3 (1) • SL-C(IAC, control system) 4: SR 1.1 3 (1) 6 FR 2 – Use control 6.1 Purpose and SL-C(UC) descriptions Enforce the assigned privileges of an authenticated user (human, software process or device) to perform the requested action on the IACS and monitor the use of these privileges. • SL 1 – Restrict use of the IACS according to specified privileges to protect against casual or coincidental misuse. • SL 2 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Restrict use of the IACS according to specified privileges to protect against circumvention by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 6.2 Rationale Once the user is identified and authenticated, the control system has to restrict the allowed actions to the authorized use of the control system. Asset owners and system integrators will have to assign, to each user (human, software process or device), group, ro le, etc. (see 5.6, SR 1.4 – Identifier management) the privileges defining the authorized use of the IACS. The goal of use control is to protect against unauthorized actions on the control system resources by verifying that the necessary privileges have been granted before a llowing a user to perform the actions. Examples of actions are reading or writing data, downloading program s and setting configurations. Recommendations and guidelines should include mechanisms that will operate in mixed modes. For example, some control system resources require strong use control protection, such as restrictive privileges, and others do not. By extension, use control requirements need to be extended to data at rest. User privileges may vary based on time- ofday/date, location and means by which access is made.
SR2.1 | SR 2.1 | Base requirement | Authorization enforcement | On all interfaces, t he control system shall provide the capability to enforce authorizations assigned to all human users for controlling use of the control system to support segregation of duties and least privilege. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4)
SR2.1.1 | SR 2.1 RE (1) | Enhancement | Authorization enforcement for all users | On all interfaces, the control system shall provide the capability to enforce authorizations assigned to all users (humans, software processes and devices) for controlling use of the control system to support segregation of duties and least privilege. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4)
SR2.1.2 | SR 2.1 RE (2) | Enhancement | Permissi on mapping to roles | The control system shall provide the capability for an authorized user or role to define and modify the mapping of permissions to roles for all human users. NOTE 1 It is a commonly accepted good practice to not limit roles to fixed nested hierarchies in which a higher level role is a superset of a lesser privileged role. For example, a system administrator generally does not necessarily encompass operator privileges. NOTE 2 This RE is applicable to software processes and devices as w ell. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4)
SR2.1.3 | SR 2.1 RE (3) | Enhancement | Supervisor override | The control system shall support supervisor manual override of the current human user authorizations for a configurable time or event sequence. NOTE Implementation of a controlled, audited and manual override of automated mechanisms in the event of emergencies or other serious events is often needed. This allows a supervisor to enable an operator to quickly react to unusual conditions without closing the current session and establishing a new session as a higher privil ege human user. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4)
SR2.1.4 | SR 2.1 RE (4) | Enhancement | Dual approval | The control system shall support dual approval where an action can result in serious impact on the industrial process. NOTE It is a commonly accepted good practice to limit dual approval to actions which require a very high level of confidence that they will be performed reliably and correctly. Requiring dual approval provides emphasis to the seriousness of consequences that would result from failure of a correct action. An example of a situation in which dual approval is required would be a change to a set point of a critical industrial process. It is a commonly accepted good practice to not employ dual approval mechanisms when an immediate response is necessary to safeguard HSE consequences, for example, emergency shutdown of an industrial process. | Use control policies (for example, identity -based policies, role- based policies and rule- based policies) and associated read/write access enforcement mechanisms (for example, access control lists, access control matrices and cryptography) are employed to control usage between users (humans, software processes and devices) and assets (for example, devices, files, records, software pr ocesses, programs and domains). After the control system has verified the identity of a user (human, software process or device) (see 5.3, SR 1.1 – Human user identification and authentication and 5.4, SR 1.2 – Software process and device identification and authentication), it also has to verify that a requested operation is actually permitted according to the defined security policies and procedures. For example, in a role- based access control policy, the control system would check which roles are assigned to a verified user or asset and which privileges are assigned to these roles – if the requested operation is covered by the permissions, it is executed, otherwise rejected. This allows the enforcement of segregation of duties and least privileges. Usage enforcement mec hanisms should not be allowed to adversely affect the operational performance of the control system. Planned or unplanned changes to control system components can have significant effects on the overall security of the control system. Accordingly, only qua lified and authorized individuals should obtain the use of control system components for purposes of initiating changes, including upgrades and modifications. | The requirements for the four SL levels that relate to SR 2.1 – Authorization enforcement are: • SL-C(UC, control system) 1: SR 2. 1 • SL-C(UC, control system) 2: SR 2.1 (1) (2) • SL-C(UC, control system) 3: SR 2.1 (1) (2) (3) • SL-C(UC, control system) 4: SR 2.1 (1) (2) (3) (4)
SR2.2 | SR 2.2 | Base requirement | W ireless use control | The control system shall provide the capability to authorize, monitor and enforce usage restrictions for wireless connectivity to the control system according to commonly accepted security industry practices. | Any wireless technology can, and in most cases should, be considered just another communication protocol option, and thus subject to the same IACS security requirements as any other communication type utilized by the IACS. However, a risk analysis may result in a requirement for wireless IACS components to support higher use control capabilities than are typically required of wired systems for the same use case and SL-T. Regulatory differences may also result in different required capa bilities between wired and wireless communications. As noted in 5.8, SR 1.6 – Wireless access management, wireless technologies include, but are not limited to, microwave, satellite, packet radio, IEEE 802.11x, IEEE 802.15.4 (ZigBee, IEC 62591 – Wireless HART®, ISA -100.11a), IEEE 802.15.1 (Bluetooth), wireless LAN mobile routers, mobile phones with tethering and various infrared technologies. | The requirements for the four SL levels that relate to SR 2.2 – Wireless use control are: • SL-C(UC, control system) 1: SR 2.2 • SL-C(UC, control system) 2: SR 2. 2 • SL-C(UC, control system) 3: SR 2. 2 (1) • SL-C(UC, control system) 4: SR 2. 2 (1)
SR2.2.1 | SR 2.2 RE (1) | Enhancement | Identify and report unauthorized wireless devices | The control system shall provide the capability to identify and report unauthorized wireless devices transmitting within the control system physical environment. 6.4.3.2 Void | Any wireless technology can, and in most cases should, be considered just another communication protocol option, and thus subject to the same IACS security requirements as any other communication type utilized by the IACS. However, a risk analysis may result in a requirement for wireless IACS components to support higher use control capabilities than are typically required of wired systems for the same use case and SL-T. Regulatory differences may also result in different required capa bilities between wired and wireless communications. As noted in 5.8, SR 1.6 – Wireless access management, wireless technologies include, but are not limited to, microwave, satellite, packet radio, IEEE 802.11x, IEEE 802.15.4 (ZigBee, IEC 62591 – Wireless HART®, ISA -100.11a), IEEE 802.15.1 (Bluetooth), wireless LAN mobile routers, mobile phones with tethering and various infrared technologies. | The requirements for the four SL levels that relate to SR 2.2 – Wireless use control are: • SL-C(UC, control system) 1: SR 2.2 • SL-C(UC, control system) 2: SR 2. 2 • SL-C(UC, control system) 3: SR 2. 2 (1) • SL-C(UC, control system) 4: SR 2. 2 (1)
SR2.3 | SR 2.3 | Base requirement | Use control for portable and mobile devices | The control system shall provide the capability to automatically enforce configurable usage restrictions that include: a) preventing the use of portable and mobile devices; b) requiring context specific authorization; and c) restricting code and data transfer to/from portable and mobile devices. | Portable and mobile devices may introduce undesired network traffic, malware and/or information exposure, so there should be spec ific control associated with their usage in the typical control system environment. Security policies and procedures may not allow c ertain functions or activities via portable and/or mobile devices. Refer to IEC 62443‑2‑1 for guidance on when and where portable and mobile devices usage should be permitted. Protecting information residing on portable and mobile devices (for example, employing cryptographic mechanisms to provide confidentiality and integrity protecti ons during storage and while in transit when outside of controlled areas) is covered elsewhere (see Clause 8, FR 4 – Data confidentiality). | The requirements for the four S L levels that relate to SR 2.3 – Use control for portable and mobile devices are: • SL-C(UC, control system) 1: SR 2.3 • SL-C(UC, control system) 2: SR 2. 3 • SL-C(UC, control system) 3: SR 2. 3 (1) • SL-C(UC, control system) 4: SR 2. 3 (1)
SR2.3.1 | SR 2.3 RE (1) | Enhancement | Enforcement of security status o f portable and mobile devices | The control system shall provide the capability to verify that portable or mobile devices attempting to connect to a zone compl y with the security requirements of that zone. 6.5.3.2 Void | Portable and mobile devices may introduce undesired network traffic, malware and/or information exposure, so there should be spec ific control associated with their usage in the typical control system environment. Security policies and procedures may not allow c ertain functions or activities via portable and/or mobile devices. Refer to IEC 62443‑2‑1 for guidance on when and where portable and mobile devices usage should be permitted. Protecting information residing on portable and mobile devices (for example, employing cryptographic mechanisms to provide confidentiality and integrity protecti ons during storage and while in transit when outside of controlled areas) is covered elsewhere (see Clause 8, FR 4 – Data confidentiality). | The requirements for the four S L levels that relate to SR 2.3 – Use control for portable and mobile devices are: • SL-C(UC, control system) 1: SR 2.3 • SL-C(UC, control system) 2: SR 2. 3 • SL-C(UC, control system) 3: SR 2. 3 (1) • SL-C(UC, control system) 4: SR 2. 3 (1)
SR2.4 | SR 2.4 | Base requirement | Mobile code | The control system shall provide the capability to enforce usage restrictions for mobile code technologies based on the potential t o cause damage to the c ontrol system that includ e: a) preventing the execution of mobile code; b) requiring proper authentication and authorization for origin of the code; c) restricting mobile code transfer to/from the control system; and d) monitoring the use of mobile code. | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, portable document format (PDF), Postscript, Shockwave movies, F lash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and execut ed on individual workstations. Control procedures should preve nt the development, acquisition or introduction of unacceptabl e mobile code within the control system. For example, mobile code exchanges may be disallowed directly with the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to SR 2.4 – Mobile code are: • SL-C(UC, control system) 1: SR 2.4 • SL-C(UC, control system) 2: SR 2. 4 • SL-C(UC, control system) 3: SR 2. 4 (1) • SL-C(UC, control system) 4: SR 2. 4 (1)
SR2.4.1 | SR 2.4 RE (1) | Enhancement | Mobile code integrity check | The control system shall provide the capability to verify integrity of the mobile code before allowing code execution. 6.6.3.2 Void | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, portable document format (PDF), Postscript, Shockwave movies, F lash animations and VBScript. Usage restrictions apply to both the selection and use of mobile code installed on servers and mobile code downloaded and execut ed on individual workstations. Control procedures should preve nt the development, acquisition or introduction of unacceptabl e mobile code within the control system. For example, mobile code exchanges may be disallowed directly with the control system, but may be allowed in a controlled adjacent environment maintained by IACS personnel. | The requirements for the four SL levels that relate to SR 2.4 – Mobile code are: • SL-C(UC, control system) 1: SR 2.4 • SL-C(UC, control system) 2: SR 2. 4 • SL-C(UC, control system) 3: SR 2. 4 (1) • SL-C(UC, control system) 4: SR 2. 4 (1)
SR2.5 | SR 2.5 | Base requirement | Session lock | The control system shall provide the capability to prevent further access by initiating a session lock after a configurable time period of inactivity or by manual initiation. The session lock shall remain in effect until the human user who owns the session or another author ized human user re-establishes access using appropriate identification and authentication procedures. | The entity responsible for a control system should employ session lock to prevent access to specified workstations or nodes. The control system should activate session lock mechanisms automatically after a configurable time period for designated workstations or nodes. In some cases, session lock for control system operator workstations or nodes is not advised (for example, sessions which are required for immediate operator responses in emergency situations). Session locks are not a substitute for logging out of the control system. In situations where the control system cannot support session lock, the responsible entity sh ould employ appropriate compensating countermeasures (for example, providing increased physical security, personnel security and auditing measures). | The requirements for the four SL levels that relate to SR 2.5 – Session lock are: • SL-C(UC, control system) 1: SR 2.5 • SL-C(UC, control system) 2: SR 2.5 • SL-C(UC, control system) 3: SR 2.5 • SL-C(UC, control system) 4: SR 2.5
SR2.6 | SR 2.6 | Base requirement | Remote session termination | The control system shall provide the capability to terminate a remote session either automatically after a configurable time period of inactivity or manually by the user who initiated the session. | A remote session is initiated whenever a control system is accessed across the boundary of a zone defined by the asset owner based on their risk assessment. This requirement may be limited to sessions that are used for control system monitoring and maintenance activities (not critical operations) based on the r isk assessment of the control system and security polic ies and procedures. Some control systems or components may not allow sessions to be terminated. | The requirements for the four SL levels that relate to SR 2.6 – Remote session termination are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: SR 2. 6 • SL-C(UC, control system) 3: SR 2. 6 • SL-C(UC, control system) 4: SR 2. 6
SR2.7 | SR 2.7 | Base requirement | Concurrent session control | The control system shall provide the capability to limit the number of concurrent sessions per interface for any given user (human, software process or device) to a configurable number of sessions. | A resource starvation DoS might occur if a limit is not imposed. There is a trade- off between potentially locking out a specific user versus locking out all users and services due to a lack of control system resources. Product supplier and/ or system integrator guidance is likely required to provide suffi cient information as to how the number of sessions value should be assigned. | The requirements for the four SL levels that relate to SR 2.7 – Concurrent session control are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: Not Selected • SL-C(UC, control system) 3: SR 2. 7 • SL-C(UC, control system) 4: SR 2. 7
SR2.8 | SR 2.8 | Base requirement | Auditable events | The control system shall provide the capability to generate audit records relevant to security for the following categories: access control, request errors, operating system events, control system events, backup and restore events, configuration changes, potential reconnaissance activity and audit log events. Individual audit records shall include the timestamp, source (originating device, software process or human user account), category, type, event ID and event result. | The purpose of this requirement is to record the occurrence of important events which need to be audited as significant and relevant to the security of the control system. Auditing activit y can affect control system performance. The security aud it function is usually coordinated with the network health and status monitoring function which may be in a different zone. Commonly recognized and accepted checklists and configuration guides should be considered when compili ng a list of auditable events. The security policies and procedures should define auditable events that are adequate to support after -the-fact investigations of security incidents. In addition, audit records should be sufficient to monitor the effectiveness and proper operation of the security mechanisms utilized to meet the requirements in this standard. It should be noted that the requirement for event recording is applicable within the given system functionality, specifically given system security requirements on a given level. For example, the requirement for recording of authentication events (in the access control category) on a SL 1 system is only applicable to the level of authentication functionality required for SL 1 according to the requirements in Clause 5. Events may occur in any control system component (for example login events) or may be observed by dedicated monitors. F or example, port scanning might be detected by an intrusion detection system (IDS) or intrusion prevention system (IPS). | The requirements for the four SL levels that relate to SR 2.8 – Auditable events are: • SL-C(UC, control system) 1: SR 2.8 • SL-C(UC, control system) 2: SR 2. 8 • SL-C(UC, control system) 3: SR 2. 8 (1) • SL-C(UC, control system) 4: SR 2. 8 (1)
SR2.8.1 | SR 2.8 RE (1) | Enhancement | Centrally managed, system -wide audit trail | The control system shall provide the capability to centrally manage audit events and to compile audit records from multiple components throughout the control system into a system - wide (logical or physical), time -correlated audit trail. The control system shall provide the capability to export these audit records in industry standard formats for analysis by standard commercial log analysis tools, for example, security information and event management (SIEM). 6.10.3.2 Void | The purpose of this requirement is to record the occurrence of important events which need to be audited as significant and relevant to the security of the control system. Auditing activit y can affect control system performance. The security aud it function is usually coordinated with the network health and status monitoring function which may be in a different zone. Commonly recognized and accepted checklists and configuration guides should be considered when compili ng a list of auditable events. The security policies and procedures should define auditable events that are adequate to support after -the-fact investigations of security incidents. In addition, audit records should be sufficient to monitor the effectiveness and proper operation of the security mechanisms utilized to meet the requirements in this standard. It should be noted that the requirement for event recording is applicable within the given system functionality, specifically given system security requirements on a given level. For example, the requirement for recording of authentication events (in the access control category) on a SL 1 system is only applicable to the level of authentication functionality required for SL 1 according to the requirements in Clause 5. Events may occur in any control system component (for example login events) or may be observed by dedicated monitors. F or example, port scanning might be detected by an intrusion detection system (IDS) or intrusion prevention system (IPS). | The requirements for the four SL levels that relate to SR 2.8 – Auditable events are: • SL-C(UC, control system) 1: SR 2.8 • SL-C(UC, control system) 2: SR 2. 8 • SL-C(UC, control system) 3: SR 2. 8 (1) • SL-C(UC, control system) 4: SR 2. 8 (1)
SR2.9 | SR 2.9 | Base requirement | Audit storage capacity | The control system shall allocate sufficient audit record storage capacity according to commonly recognized recommendations for log management and system configuration. The control system shall provide auditing mechanisms to reduce the likelihood of such capacity being exceeded. | The control system should provide sufficient audit storage capacity, taking into account retention policy, the auditing to be performed and the online audit processing requirements. Guidelines to be considered could include the NIST Special Publication (SP) 800-92 [27]. The audit storage capacity should be sufficient to retain logs for a period of time required by applicable policies and regulations or business requirements. | The requirements for the four SL levels that relate to SR 2.9 – Audit storage capacity are: • SL-C(UC, control system) 1: SR 2.9 • SL-C(UC, control system) 2: SR 2.9 • SL-C(UC, control system) 3: SR 2.9 (1) • SL-C(UC, control system) 4: SR 2.9 (1)
SR2.9.1 | SR 2.9 RE (1) | Enhancement | Warn when audit record storage capacity threshold reached | The control system shall provide the capability to issue a warning when the allocated audit record storage volume reaches a configurable percentage of maximu m audit record storage capacity. 6.11.3.2 Void | The control system should provide sufficient audit storage capacity, taking into account retention policy, the auditing to be performed and the online audit processing requirements. Guidelines to be considered could include the NIST Special Publication (SP) 800-92 [27]. The audit storage capacity should be sufficient to retain logs for a period of time required by applicable policies and regulations or business requirements. | The requirements for the four SL levels that relate to SR 2.9 – Audit storage capacity are: • SL-C(UC, control system) 1: SR 2.9 • SL-C(UC, control system) 2: SR 2.9 • SL-C(UC, control system) 3: SR 2.9 (1) • SL-C(UC, control system) 4: SR 2.9 (1)
SR2.10 | SR 2.10 | Base requirement | Response to audit processing failures | The control system shall provide the capability to alert personnel and prevent the loss of essential services and functions in the event of an audit processing failure. The control system shall provide the capability to support appropriate actions in response to an audit processing failure according to commonly accepted industry practices and recommendations. | Audit generation typically occurs at the source of the event. Audit processing involves transmission, possible augmentation (such as the addition of a timestamp) and persistent storage of the audit records. Audit processing failures include, for example, software or hardware errors, failures in the audit capturing mechanisms and audit storage capac ity being reached or exceeded. Guidelines to be considered when designing appropriate response actions may include the NIST SP800 -92. It should be noted that either overwriting the oldest audit records or halting audit log generation are possible responses to audit storage capacity being exceeded but imply the loss of potentially essential forensic information. | The requirements for the four SL levels that relate to SR 2.10 – Response to audit processing failures are: • SL-C(UC, control system) 1: SR 2. 10 • SL-C(UC, control system) 2: SR 2. 10 • SL-C(UC, control system) 3: SR 2. 10 • SL-C(UC, control system) 4: SR 2. 10
SR2.11 | SR 2.11 | Base requirement | Timestamps | The control system shall provide timestamps for use in audit record generation. | Timestamps (including date and time) of audit records should be generated using internal system clocks. If system- wide time synchronization is not present (which is typical in many installations), known offsets would be needed to support analysis of a sequence of events. In addition, synchronization of internally generated audit records with external events might requ ire synchronization with a generally recognized external time source (such as the Global Positioning S ystem (GPS), Global Navigation Satellite System (GLONASS) and Galileo). The time source should be protected from unauthorized alteration. | The requirements for the four SL levels that relate to SR 2.11 – Timestamps are: • SL-C(UC, control system) 1: Not selected • SL-C(UC, control system) 2: SR 2. 11 • SL-C(UC, control system) 3: SR 2. 11 (1) • SL-C(UC, control system) 4: SR 2. 11 (1) (2) 6.14 SR 2.1 2 – Non-repudiation Requirement 6.14.1The control system shall provide the capability to determine whether a given human user took a particular action. Rationale and supplemental guidance 6.14.2 Examples of particular actions taken by a user include performing operator actions, changing control system configurations, creating information, sending a message, approving information (such as indicating concurre nce) and receiving a message. Non -repudiation protects against later false claims by a user of not having taken a specific action, by an author of not having authored a particular document, by a sender of not having transmitted a message, by a receiver of not having received a message or by a signatory of not having signed a document. Non- repudiation services can be used to determine if information originated from a user, if a user took specific actions (for example, sending an email and approving a work order) or received specific information. Non- repudiation services are obtained by employing various techniques or mechanisms (for ex ample, digital signatures, digital message receipts and timestamps). Requirement enhancements 6.14.3 6.14.3.1 SR 2.12 RE 1 – Non-repudiation for all users The control system shall provide the capability to determine whether a given user (human, software process or device) took a particular action. 6.14.3.2 Void Security levels 6.14.4 The requirements for the four SL levels that relate to SR 2.12 – Non-repudiation are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: Not Selected • SL-C(UC, control system) 3: SR 2.1 2 • SL-C(UC, control system) 4: SR 2.1 2 (1) 7 FR 3 – System integrity 7.1 Purpose and SL -C(SI) descriptions Ensure the integrity of the IACS to prevent unauthorized manipulation. • SL 1 – Protect the integrity of the IACS against casual or coincidental manipulation. • SL 2 – Protect the integrity of the IACS against manipulation by someone using simple means with low resources, generic skills and low motivation. • SL 3 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with extended resources, IACS specific skills and high motivation. 7.2 Rationale IACS often go through multiple testing cycles (unit testing, factory acceptance testing (FAT), site acceptance testing (S AT), certification, commissioning, etc.) to establish that the systems will perform as intended before they even begin production. Once operational, asset owners are responsible for maintaining the integrity of the IACS. Using their risk assessment methodo logy, asset owners may assign different levels of integrity protection to different systems, communication channels and information in their IACS. The integrity of physical assets should be maintained in both operational and non -operational states, such as during production, when in storage or during a maintenance shutdown. The integrity of logical assets should be maintained while in transit and at rest, such as being transmitted over a network or when residing in a data repository.
SR2.11.1 | SR 2.11 RE (1) | Enhancement | Internal time synchronization | The control system shall provide the capability to synchronize internal system clocks at a configurable frequency. | Timestamps (including date and time) of audit records should be generated using internal system clocks. If system- wide time synchronization is not present (which is typical in many installations), known offsets would be needed to support analysis of a sequence of events. In addition, synchronization of internally generated audit records with external events might requ ire synchronization with a generally recognized external time source (such as the Global Positioning S ystem (GPS), Global Navigation Satellite System (GLONASS) and Galileo). The time source should be protected from unauthorized alteration. | The requirements for the four SL levels that relate to SR 2.11 – Timestamps are: • SL-C(UC, control system) 1: Not selected • SL-C(UC, control system) 2: SR 2. 11 • SL-C(UC, control system) 3: SR 2. 11 (1) • SL-C(UC, control system) 4: SR 2. 11 (1) (2) 6.14 SR 2.1 2 – Non-repudiation Requirement 6.14.1The control system shall provide the capability to determine whether a given human user took a particular action. Rationale and supplemental guidance 6.14.2 Examples of particular actions taken by a user include performing operator actions, changing control system configurations, creating information, sending a message, approving information (such as indicating concurre nce) and receiving a message. Non -repudiation protects against later false claims by a user of not having taken a specific action, by an author of not having authored a particular document, by a sender of not having transmitted a message, by a receiver of not having received a message or by a signatory of not having signed a document. Non- repudiation services can be used to determine if information originated from a user, if a user took specific actions (for example, sending an email and approving a work order) or received specific information. Non- repudiation services are obtained by employing various techniques or mechanisms (for ex ample, digital signatures, digital message receipts and timestamps). Requirement enhancements 6.14.3 6.14.3.1 SR 2.12 RE 1 – Non-repudiation for all users The control system shall provide the capability to determine whether a given user (human, software process or device) took a particular action. 6.14.3.2 Void Security levels 6.14.4 The requirements for the four SL levels that relate to SR 2.12 – Non-repudiation are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: Not Selected • SL-C(UC, control system) 3: SR 2.1 2 • SL-C(UC, control system) 4: SR 2.1 2 (1) 7 FR 3 – System integrity 7.1 Purpose and SL -C(SI) descriptions Ensure the integrity of the IACS to prevent unauthorized manipulation. • SL 1 – Protect the integrity of the IACS against casual or coincidental manipulation. • SL 2 – Protect the integrity of the IACS against manipulation by someone using simple means with low resources, generic skills and low motivation. • SL 3 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with extended resources, IACS specific skills and high motivation. 7.2 Rationale IACS often go through multiple testing cycles (unit testing, factory acceptance testing (FAT), site acceptance testing (S AT), certification, commissioning, etc.) to establish that the systems will perform as intended before they even begin production. Once operational, asset owners are responsible for maintaining the integrity of the IACS. Using their risk assessment methodo logy, asset owners may assign different levels of integrity protection to different systems, communication channels and information in their IACS. The integrity of physical assets should be maintained in both operational and non -operational states, such as during production, when in storage or during a maintenance shutdown. The integrity of logical assets should be maintained while in transit and at rest, such as being transmitted over a network or when residing in a data repository.
SR2.11.2 | SR 2.11 RE (2) | Enhancement | Protection of time source integrity | The time source shall be protected from unauthorized alteration and shall cause an audit event upon alteration. | Timestamps (including date and time) of audit records should be generated using internal system clocks. If system- wide time synchronization is not present (which is typical in many installations), known offsets would be needed to support analysis of a sequence of events. In addition, synchronization of internally generated audit records with external events might requ ire synchronization with a generally recognized external time source (such as the Global Positioning S ystem (GPS), Global Navigation Satellite System (GLONASS) and Galileo). The time source should be protected from unauthorized alteration. | The requirements for the four SL levels that relate to SR 2.11 – Timestamps are: • SL-C(UC, control system) 1: Not selected • SL-C(UC, control system) 2: SR 2. 11 • SL-C(UC, control system) 3: SR 2. 11 (1) • SL-C(UC, control system) 4: SR 2. 11 (1) (2) 6.14 SR 2.1 2 – Non-repudiation Requirement 6.14.1The control system shall provide the capability to determine whether a given human user took a particular action. Rationale and supplemental guidance 6.14.2 Examples of particular actions taken by a user include performing operator actions, changing control system configurations, creating information, sending a message, approving information (such as indicating concurre nce) and receiving a message. Non -repudiation protects against later false claims by a user of not having taken a specific action, by an author of not having authored a particular document, by a sender of not having transmitted a message, by a receiver of not having received a message or by a signatory of not having signed a document. Non- repudiation services can be used to determine if information originated from a user, if a user took specific actions (for example, sending an email and approving a work order) or received specific information. Non- repudiation services are obtained by employing various techniques or mechanisms (for ex ample, digital signatures, digital message receipts and timestamps). Requirement enhancements 6.14.3 6.14.3.1 SR 2.12 RE 1 – Non-repudiation for all users The control system shall provide the capability to determine whether a given user (human, software process or device) took a particular action. 6.14.3.2 Void Security levels 6.14.4 The requirements for the four SL levels that relate to SR 2.12 – Non-repudiation are: • SL-C(UC, control system) 1: Not Selected • SL-C(UC, control system) 2: Not Selected • SL-C(UC, control system) 3: SR 2.1 2 • SL-C(UC, control system) 4: SR 2.1 2 (1) 7 FR 3 – System integrity 7.1 Purpose and SL -C(SI) descriptions Ensure the integrity of the IACS to prevent unauthorized manipulation. • SL 1 – Protect the integrity of the IACS against casual or coincidental manipulation. • SL 2 – Protect the integrity of the IACS against manipulation by someone using simple means with low resources, generic skills and low motivation. • SL 3 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Protect the integrity of the IACS against manipulation by someone using sophisticated means with extended resources, IACS specific skills and high motivation. 7.2 Rationale IACS often go through multiple testing cycles (unit testing, factory acceptance testing (FAT), site acceptance testing (S AT), certification, commissioning, etc.) to establish that the systems will perform as intended before they even begin production. Once operational, asset owners are responsible for maintaining the integrity of the IACS. Using their risk assessment methodo logy, asset owners may assign different levels of integrity protection to different systems, communication channels and information in their IACS. The integrity of physical assets should be maintained in both operational and non -operational states, such as during production, when in storage or during a maintenance shutdown. The integrity of logical assets should be maintained while in transit and at rest, such as being transmitted over a network or when residing in a data repository.
SR3.1 | SR 3.1 | Base requirement | Communication integrity | The control system shall provide the capability to protect the integrity of transmitted information. | Many common network attacks are based on the manipulation of data in transmission, for example manipulation of network packets. Switched or routed networks provide a greater opportunity for attackers to manipulate packets as undetected access to these networks is generally easier and the switching and routing mechanisms themselves can also be manipulated in order to get more access to transmitted information. Manipulation in the context of a control system could include the change of measurement values communicated from a sensor to a receiver or the alteration of command parameters sent from a contr ol application to an actuator. Depending on the context (for example transmission within a local network segment versus transmission via untrusted networks) and the network type used in the transmission (for example transmission control protocol (TCP) / internet protocol (IP) versus local serial links), feasible and appropriate mechanisms will vary. On a small network with direct links (point -topoint), physical access protection to all nodes may be sufficient on lower SLs if the endpoints’ integrity is pro tected as well (see 7.6, SR 3.4 – Software and information integrity), while on a network distributed in areas with regular physical presence of staff or on a wide area network physical access is likely not enforceable. If a commercial service is used to provide communication services as a commodity item rather than a fully dedicated service (for example a leased line v ersus a T1 link), it may be more difficult to obtain the necessary assurances regarding the implementation of needed security controls for communication integrity (for example because of legal restrictions). When it is infeasible or impractical to meet the necessary security requirements it may be appropriate to implement either appropriate compensating countermeasures or explicitly accept the additional risk. Industrial equipment is often subject to environmental conditions that can lead to integrity issues and/or false positive incidents. Many times the environment contains particulates, liquids, vibration, gases, radiation, and electromagnetic interference (EMI) that can cause conditions that affect the integrity of the communication wiring and signals. The network infrastructure should be designed to minimize these physical/environmental effects on communication integrity. For example, when particulate, liquids, and/or gases are an issue, it may be necessary to use a sealed registered jack 45 (RJ -45) or M12 connector instead of a commercial -grade RJ -45 connector on the wire. The cable itself may need to use a different jacket instead to handle the particulate, liquid, and/or gas as well. In cases where vibration is an issue, M12 connectors may be necessary to prevent the spring pins on an RJ -45 connector from disconnecting during use. In cases where radiation and/or EMI are an issue, it may be necessary to use shielded twisted pair or fiber cables to prevent any effect on the communication signals. It may also be necessary to perform a wireless spectrum analysis in these areas if wireless networking is planned to verify that it is a viable solution. | The requirements for the four SL levels that relate to SR 3.1 – Communication integrity are: • SL-C(S I, contr ol system) 1: SR 3.1 • SL-C(SI, control system) 2: SR 3.1 • SL-C(SI, control system) 3: SR 3.1 (1) • SL-C(SI, control system) 4: SR 3.1 (1)
SR3.1.1 | SR 3.1 RE (1) | Enhancement | Cryptographic integrity protection | The control system shall provide the capability to employ cryptographic mechanisms to recognize changes to information during communication. NOTE It is a commonly accepted good practice to determine the appropriate use of cryptographic mechanisms for message authentication and integrity after careful consideration of the security needs and the potential ramifications on system performance and capability to recover from system failure. 7.3.3.2 Void | Many common network attacks are based on the manipulation of data in transmission, for example manipulation of network packets. Switched or routed networks provide a greater opportunity for attackers to manipulate packets as undetected access to these networks is generally easier and the switching and routing mechanisms themselves can also be manipulated in order to get more access to transmitted information. Manipulation in the context of a control system could include the change of measurement values communicated from a sensor to a receiver or the alteration of command parameters sent from a contr ol application to an actuator. Depending on the context (for example transmission within a local network segment versus transmission via untrusted networks) and the network type used in the transmission (for example transmission control protocol (TCP) / internet protocol (IP) versus local serial links), feasible and appropriate mechanisms will vary. On a small network with direct links (point -topoint), physical access protection to all nodes may be sufficient on lower SLs if the endpoints’ integrity is pro tected as well (see 7.6, SR 3.4 – Software and information integrity), while on a network distributed in areas with regular physical presence of staff or on a wide area network physical access is likely not enforceable. If a commercial service is used to provide communication services as a commodity item rather than a fully dedicated service (for example a leased line v ersus a T1 link), it may be more difficult to obtain the necessary assurances regarding the implementation of needed security controls for communication integrity (for example because of legal restrictions). When it is infeasible or impractical to meet the necessary security requirements it may be appropriate to implement either appropriate compensating countermeasures or explicitly accept the additional risk. Industrial equipment is often subject to environmental conditions that can lead to integrity issues and/or false positive incidents. Many times the environment contains particulates, liquids, vibration, gases, radiation, and electromagnetic interference (EMI) that can cause conditions that affect the integrity of the communication wiring and signals. The network infrastructure should be designed to minimize these physical/environmental effects on communication integrity. For example, when particulate, liquids, and/or gases are an issue, it may be necessary to use a sealed registered jack 45 (RJ -45) or M12 connector instead of a commercial -grade RJ -45 connector on the wire. The cable itself may need to use a different jacket instead to handle the particulate, liquid, and/or gas as well. In cases where vibration is an issue, M12 connectors may be necessary to prevent the spring pins on an RJ -45 connector from disconnecting during use. In cases where radiation and/or EMI are an issue, it may be necessary to use shielded twisted pair or fiber cables to prevent any effect on the communication signals. It may also be necessary to perform a wireless spectrum analysis in these areas if wireless networking is planned to verify that it is a viable solution. | The requirements for the four SL levels that relate to SR 3.1 – Communication integrity are: • SL-C(S I, contr ol system) 1: SR 3.1 • SL-C(SI, control system) 2: SR 3.1 • SL-C(SI, control system) 3: SR 3.1 (1) • SL-C(SI, control system) 4: SR 3.1 (1)
SR3.2 | SR 3.2 | Base requirement | Malicious code protection | The control system shall provide the capability to employ protection mechanisms to prevent, detect, report and mitigate the effects of malicious code or unauthorized software. The control system shall provide the capability to update the protection mechanisms. | The control system should us e protection mechanisms to prevent, detect, mitigate and report instances of detected malicious code (for example, viruses, worms, Trojan horses and spyware) transported by electronic mail, electronic mail attachments, Internet access, removable media (for example, universal serial bus (USB) devic es, diskettes or compact disks), PDF documents, web services, network connections and infected laptops or other common means. Detection mechanisms should be able to detect integrity violations of application binari es and data files. Techniques may include, but are not limited to, binary integrity and attributes monitoring, hashing and signature techniques. Mitigation techniques may include, but are not limited to, file cleaning, quarantining, file deletion, host communication restriction and IPSs. Prevention techniques may include, but are not limited to, application blacklisting and whitelisting techniques, removable media control, sandbox techniques and specific computing platforms mechanisms such as restricted firmware update capabilities, No Execute (NX) bit, data execution prevention (DEP), address space layout randomization (ASLR), stack corruption detection and mandatory access controls. See 10.4, SR 6.2 – Continuous monitoring for an associated requirement involving control system monitoring tools and techniques. Prevention and mitigation mechanisms may include those designed for host elements (such as computers and servers) and network -based mechanisms (such as IDS s and IPS s) and those mechanisms focused on control system specific components (such as PLCs and HMIs). | The requirements for the four SL levels that relate to SR 3.2 – Malicious code protectio n are: • SL-C(SI, control system) 1: SR 3.2 • SL-C(SI, control system) 2: SR 3.2 (1) • SL-C(SI, control system) 3: SR 3.2 (1) (2) • SL-C(SI, control system) 4: SR 3.2 (1) (2)
SR3.2.1 | SR 3.2 RE (1) | Enhancement | Malicious code protection on entry and exit points | The control system shall provide the capability to employ m alicious code protection mechanisms at all entry and exit points. NOTE Such mechanisms are commonly provided on removable media, firewalls, unidirectional gateways, web servers, proxy servers or remote -access servers. | The control system should us e protection mechanisms to prevent, detect, mitigate and report instances of detected malicious code (for example, viruses, worms, Trojan horses and spyware) transported by electronic mail, electronic mail attachments, Internet access, removable media (for example, universal serial bus (USB) devic es, diskettes or compact disks), PDF documents, web services, network connections and infected laptops or other common means. Detection mechanisms should be able to detect integrity violations of application binari es and data files. Techniques may include, but are not limited to, binary integrity and attributes monitoring, hashing and signature techniques. Mitigation techniques may include, but are not limited to, file cleaning, quarantining, file deletion, host communication restriction and IPSs. Prevention techniques may include, but are not limited to, application blacklisting and whitelisting techniques, removable media control, sandbox techniques and specific computing platforms mechanisms such as restricted firmware update capabilities, No Execute (NX) bit, data execution prevention (DEP), address space layout randomization (ASLR), stack corruption detection and mandatory access controls. See 10.4, SR 6.2 – Continuous monitoring for an associated requirement involving control system monitoring tools and techniques. Prevention and mitigation mechanisms may include those designed for host elements (such as computers and servers) and network -based mechanisms (such as IDS s and IPS s) and those mechanisms focused on control system specific components (such as PLCs and HMIs). | The requirements for the four SL levels that relate to SR 3.2 – Malicious code protectio n are: • SL-C(SI, control system) 1: SR 3.2 • SL-C(SI, control system) 2: SR 3.2 (1) • SL-C(SI, control system) 3: SR 3.2 (1) (2) • SL-C(SI, control system) 4: SR 3.2 (1) (2)
SR3.2.2 | SR 3.2 RE (2) | Enhancement | Central management and reporting for malicious code | protection The control system shall provide the capability to manage malicious code protec tion mechanisms. NOTE Such mechanisms are commonly provided by endpoint infrastructure centralized management or SIEM solutions. | The control system should us e protection mechanisms to prevent, detect, mitigate and report instances of detected malicious code (for example, viruses, worms, Trojan horses and spyware) transported by electronic mail, electronic mail attachments, Internet access, removable media (for example, universal serial bus (USB) devic es, diskettes or compact disks), PDF documents, web services, network connections and infected laptops or other common means. Detection mechanisms should be able to detect integrity violations of application binari es and data files. Techniques may include, but are not limited to, binary integrity and attributes monitoring, hashing and signature techniques. Mitigation techniques may include, but are not limited to, file cleaning, quarantining, file deletion, host communication restriction and IPSs. Prevention techniques may include, but are not limited to, application blacklisting and whitelisting techniques, removable media control, sandbox techniques and specific computing platforms mechanisms such as restricted firmware update capabilities, No Execute (NX) bit, data execution prevention (DEP), address space layout randomization (ASLR), stack corruption detection and mandatory access controls. See 10.4, SR 6.2 – Continuous monitoring for an associated requirement involving control system monitoring tools and techniques. Prevention and mitigation mechanisms may include those designed for host elements (such as computers and servers) and network -based mechanisms (such as IDS s and IPS s) and those mechanisms focused on control system specific components (such as PLCs and HMIs). | The requirements for the four SL levels that relate to SR 3.2 – Malicious code protectio n are: • SL-C(SI, control system) 1: SR 3.2 • SL-C(SI, control system) 2: SR 3.2 (1) • SL-C(SI, control system) 3: SR 3.2 (1) (2) • SL-C(SI, control system) 4: SR 3.2 (1) (2)
SR3.3 | SR 3.3 | Base requirement | Security functionality verification | The control system shall provide the capability to support verification of the intended operation of security functions and report when anomalies are discovered during FAT, SAT and scheduled maintenance. These securit y functions shall include all those necessary to support the security requirements specified in this standard. | The product supplier and/or system integrator should provide guidance on how to test the designed security co ntrols. Asset owners need to be aware of the possible ramifications of running these verification tests during normal operations. Details of the execution of these verifications need to be specified with careful consideration of the requirements for contin uous operations (for example, scheduling or prior notification). Examples of security verification functions include: • Verification of antivirus measures by European Institute for Computer Antivirus Research (EICAR) testing of the control system file system. Antivirus software should detect this and appropriate incident handling procedures should be triggered. • Verification of the identification, authentication and use control measures by attempting access with an unauthorized account (for some functionality this could be automated). • Verification of IDSs as a security control by including a rule in the IDS that triggers on irregular, but known non -malicious traffic. The test could then be performed by introducing traffic that triggers this rule and the appropriate IDS monitoring and incident handling procedures. • Confirm ation that audit logging is occurring as required by security policies and procedures and has not been disabled by an internal or external entity. | The requirements for the four SL levels that relate to SR 3.3 – Security functionality verification are: • SL-C(SI, control system) 1: SR 3.3 • SL-C(SI, control system) 2: SR 3.3 • SL-C(SI, control system) 3: SR 3.3 (1) • SL-C(SI, control system) 4: SR 3.3 (1) (2)
SR3.3.1 | SR 3.3 RE (1) | Enhancement | Automated mechanisms for security functionality verification | The control system shall provide the capability to employ automated mechanisms to support management of security verification during FAT, SAT and scheduled maintenance. | The product supplier and/or system integrator should provide guidance on how to test the designed security co ntrols. Asset owners need to be aware of the possible ramifications of running these verification tests during normal operations. Details of the execution of these verifications need to be specified with careful consideration of the requirements for contin uous operations (for example, scheduling or prior notification). Examples of security verification functions include: • Verification of antivirus measures by European Institute for Computer Antivirus Research (EICAR) testing of the control system file system. Antivirus software should detect this and appropriate incident handling procedures should be triggered. • Verification of the identification, authentication and use control measures by attempting access with an unauthorized account (for some functionality this could be automated). • Verification of IDSs as a security control by including a rule in the IDS that triggers on irregular, but known non -malicious traffic. The test could then be performed by introducing traffic that triggers this rule and the appropriate IDS monitoring and incident handling procedures. • Confirm ation that audit logging is occurring as required by security policies and procedures and has not been disabled by an internal or external entity. | The requirements for the four SL levels that relate to SR 3.3 – Security functionality verification are: • SL-C(SI, control system) 1: SR 3.3 • SL-C(SI, control system) 2: SR 3.3 • SL-C(SI, control system) 3: SR 3.3 (1) • SL-C(SI, control system) 4: SR 3.3 (1) (2)
SR3.3.2 | SR 3.3 RE (2) | Enhancement | Security functionality verification during normal operation | The control system shall provide the capability to support verification of the intended operation of security functions during normal operations. NOTE It is a commonly accepted good practice to carefully implement this requirement as it can lead to detrimental effects. It is often not considered suitable for safety systems. | The product supplier and/or system integrator should provide guidance on how to test the designed security co ntrols. Asset owners need to be aware of the possible ramifications of running these verification tests during normal operations. Details of the execution of these verifications need to be specified with careful consideration of the requirements for contin uous operations (for example, scheduling or prior notification). Examples of security verification functions include: • Verification of antivirus measures by European Institute for Computer Antivirus Research (EICAR) testing of the control system file system. Antivirus software should detect this and appropriate incident handling procedures should be triggered. • Verification of the identification, authentication and use control measures by attempting access with an unauthorized account (for some functionality this could be automated). • Verification of IDSs as a security control by including a rule in the IDS that triggers on irregular, but known non -malicious traffic. The test could then be performed by introducing traffic that triggers this rule and the appropriate IDS monitoring and incident handling procedures. • Confirm ation that audit logging is occurring as required by security policies and procedures and has not been disabled by an internal or external entity. | The requirements for the four SL levels that relate to SR 3.3 – Security functionality verification are: • SL-C(SI, control system) 1: SR 3.3 • SL-C(SI, control system) 2: SR 3.3 • SL-C(SI, control system) 3: SR 3.3 (1) • SL-C(SI, control system) 4: SR 3.3 (1) (2)
SR3.4 | SR 3.4 | Base requirement | Software and information integrity | The control system shall provide the capability to detect, record, report and protect against unauthorized change s to software and information at rest. | Unauthorized changes are changes for which the entity attempting the change does not have the required privileges. This SR complements related SRs from FRs 1 and 2. FRs 1 and 2 involve enforcing the roles, privileges and use patterns as designed. Integrity verification methods are employed to detect, record, report and protect against software and information tampering that may occur if other protection mechanisms (such as authorization enforcement) have been circumvented. The control system should employ formal or recommended integrity mechanisms (such as cryptographic hashes). For example, such mechanisms could be used to monitor field devices for their latest configuration information to detect security breaches (including unauthorized changes). | The requirements for the four SL levels that relate to SR 3.4 – Software and information integrity are:  SL-C(SI, control system) 1: Not selected  SL-C(SI, control system) 2: SR 3.4  SL-C(SI, control system) 3: SR 3.4 (1)  SL-C(SI, control system) 4: SR 3.4 (1)
SR3.4.1 | SR 3.4 RE (1) | Enhancement | Automated notification about integrity violations | The control system shall provide the capability to use automated tools that provide notification to a configurable set of recipients upon discovering discrepancies during integrity verification. 7.6.3.2 Void | Unauthorized changes are changes for which the entity attempting the change does not have the required privileges. This SR complements related SRs from FRs 1 and 2. FRs 1 and 2 involve enforcing the roles, privileges and use patterns as designed. Integrity verification methods are employed to detect, record, report and protect against software and information tampering that may occur if other protection mechanisms (such as authorization enforcement) have been circumvented. The control system should employ formal or recommended integrity mechanisms (such as cryptographic hashes). For example, such mechanisms could be used to monitor field devices for their latest configuration information to detect security breaches (including unauthorized changes). | The requirements for the four SL levels that relate to SR 3.4 – Software and information integrity are:  SL-C(SI, control system) 1: Not selected  SL-C(SI, control system) 2: SR 3.4  SL-C(SI, control system) 3: SR 3.4 (1)  SL-C(SI, control system) 4: SR 3.4 (1)
SR3.5 | SR 3.5 | Base requirement | Input validation | The control system shall validate the syntax and content of any input which is used as an industrial process control input or input that directly impacts the action of the control system. | Rules for checking the valid syntax of control system inputs such as set points should be in place to verify that this information has not been tampered with and is compliant with the specification. Inputs passed to interpreters should be pre-screened to prevent the content from being unintentionally interpreted as commands. Note that this is a security SR, thus it does not address human error, for example supplying a legitimate integer number which is outside the expected range. Generally accepted industry practices for input data validation include out-of-range values for a defined field type, invalid characters in data fields, missing or incomplete data and buffer overflow. Additional examples where invalid inputs lead to system security issues include SQL injection attacks, cross-site scripting or ma lformed packets (as commonly generated by protocol fuzzers). Guidelines to be considered could include the Open Web Application Security Project (OWASP) [31] Code Review Guide. | The requirements for the four SL levels that relate to SR 3.5 – Input validation are:  SL-C(SI, control system) 1: SR 3.5  SL-C(SI, control system) 2: SR 3.5  SL-C(SI, control system) 3: SR 3.5  SL-C(SI, control system) 4: SR 3.5
SR3.6 | SR 3.6 | Base requirement | Deterministic output | The control system shall provide the capability to set outputs to a predetermined state if normal operation cannot be maintained as a result of an attack. | The deterministic behavior of control system outputs as a result of threat actions against the control system is an important characteristic to ensure the integrity of normal operations. Ideally, the control system continues to operate normally while under attack, but if the control system cannot maintain normal operation, then the control system outputs need to fail to a predetermined state. The appropriate predetermined state of control system outputs is application dependent and could be one of the following user configurable options: • Unpowered – the outputs fail to the unpowered state • Hold – the outputs fail to the last -known good value • Fixed – the outputs fail to a fixed value that is determined by the asset owner or an application | The requirements for the four SL levels that relate to SR 3.6 – Deterministic output are: • SR-C(SI, control system) 1: SR 3.6 • SR-C(SI, control system) 2: SR 3.6 • SR-C(SI, control system) 3: SR 3.6 • SR-C(SI, control system) 4: SR 3.6
SR3.7 | SR 3.7 | Base requirement | Error handling | The control system shall identify and handle error conditions in a manner such that effective remediation can occur. This shall be done in a manner which does not provide information that could be exploited by adversaries to attack the IACS unless revealing this information is necessary for the timely troubleshooting of problems. | The structure and content of error messages should be carefully considered by the product supplier and/or syste m integrator. Error messages generated by the control system should provide timely and useful information without revealing potentially harmful inform ation that could be used by adversaries to exploit the IACS. Since it may be unclear whether a particular error condition is due to a security event, all error messages may need to be easily accessible during incident response. Disclosure of this information should be justified by the necessity for timely resolution of error conditions. Guidelines to be considered could include the OWASP Code Review Guide [31]. | The requirements for the four SL levels that relat e to SR 3.7 – Error handling are: • SL-C(SI, control system) 1: Not Selected • SL-C(SI, control system) 2: SR 3. 7 • SL-C(SI, control system) 3: SR 3.7 • SL-C(SI, control system) 4: SR 3. 7
SR3.8 | SR 3.8 | Base requirement | Session integrity | The control system shall provide the capability to protect the integrity of sessions. The control system shall reject any usage of invalid session IDs. | This control focuses on communications protection at the session, versus packet, level. The intent of this control is to establish grounds for confidence at each end of a communications session in the ongoing identity of the other party and in the validity of the information being transmitted. For example, this control addresses man- in-the-middle attacks including session hijacking, insertion of false information into a session or replay attacks. Use of session integrity mechanisms can have a significant overhead and therefore their use should be considered in light of requirements for real-time communications. | The requirements for the four SL levels that relate to SR 3.8 – Session integrity are: • SL-C(SI, control system) 1: Not Selected • SL-C(SI, control system) 2: SR 3. 8 • SL-C(SI, control system) 3: SR 3. 8 (1) (2) • SL-C(SI, control system) 4: SR 3. 8 (1) (2) (3)
SR3.8.1 | SR 3.8 RE (1) | Enhancement | Invalidation of session IDs after session termination | The control system shall provide the capability to invalidate session IDs upon user logout or other session termination (including browser sessions). | This control focuses on communications protection at the session, versus packet, level. The intent of this control is to establish grounds for confidence at each end of a communications session in the ongoing identity of the other party and in the validity of the information being transmitted. For example, this control addresses man- in-the-middle attacks including session hijacking, insertion of false information into a session or replay attacks. Use of session integrity mechanisms can have a significant overhead and therefore their use should be considered in light of requirements for real-time communications. | The requirements for the four SL levels that relate to SR 3.8 – Session integrity are: • SL-C(SI, control system) 1: Not Selected • SL-C(SI, control system) 2: SR 3. 8 • SL-C(SI, control system) 3: SR 3. 8 (1) (2) • SL-C(SI, control system) 4: SR 3. 8 (1) (2) (3)
SR3.8.2 | SR 3.8 RE (2) | Enhancement | Unique session ID generation | The control system shall provide the capability to generate a unique session ID for each session and treat all unexpected session IDs as invalid. | This control focuses on communications protection at the session, versus packet, level. The intent of this control is to establish grounds for confidence at each end of a communications session in the ongoing identity of the other party and in the validity of the information being transmitted. For example, this control addresses man- in-the-middle attacks including session hijacking, insertion of false information into a session or replay attacks. Use of session integrity mechanisms can have a significant overhead and therefore their use should be considered in light of requirements for real-time communications. | The requirements for the four SL levels that relate to SR 3.8 – Session integrity are: • SL-C(SI, control system) 1: Not Selected • SL-C(SI, control system) 2: SR 3. 8 • SL-C(SI, control system) 3: SR 3. 8 (1) (2) • SL-C(SI, control system) 4: SR 3. 8 (1) (2) (3)
SR3.8.3 | SR 3.8 RE (3) | Enhancement | Randomness of session IDs | The control system shall provide the capability to generate unique session IDs with commonly accepted sources of randomness. NOTE Session hijacking and other man- in-the-middle attacks or injections of false information often take advantage of easy -to-guess session IDs (keys or other shared secrets) or use of session IDs which were not properly invalidated after session termination. Therefore the validity of a session authenticator needs to be tightly connected to the lifetime of a session. Employing randomness in the generation of unique session IDs helps to protect against brute- force attacks to determine future session IDs. | This control focuses on communications protection at the session, versus packet, level. The intent of this control is to establish grounds for confidence at each end of a communications session in the ongoing identity of the other party and in the validity of the information being transmitted. For example, this control addresses man- in-the-middle attacks including session hijacking, insertion of false information into a session or replay attacks. Use of session integrity mechanisms can have a significant overhead and therefore their use should be considered in light of requirements for real-time communications. | The requirements for the four SL levels that relate to SR 3.8 – Session integrity are: • SL-C(SI, control system) 1: Not Selected • SL-C(SI, control system) 2: SR 3. 8 • SL-C(SI, control system) 3: SR 3. 8 (1) (2) • SL-C(SI, control system) 4: SR 3. 8 (1) (2) (3)
SR3.9 | SR 3.9 | Base requirement | Protection of audit information | The control system shall protect audit information and audit tools (if present) from unauthorized access, modification and deletion. | Audit information includes all information (for example, audit records, audit settings and audit reports) needed to successfully audit control system activity. The audit information is important for error correction, security breach recovery, investigations and related efforts. Mechanisms for enhanced protection against modification and deletion include the storage of audit information to hardware- enforced write- once media. | The requirements for the four SL levels that relate to SR 3.9 – Protection of audit information are: • SL-C(SI, control system) 1: Not selected • SL-C(SI, control system) 2: SR 3.9 • SL-C(SI, control system) 3: SR 3.9 • SL-C(SI, control system) 4: SR 3.9 (1) 8 FR 4 – Data confidentiality 8.1 Purpose and SL-C(DC) descriptions Ensure the confidentiality of information on communication channels and in data repositories to prevent unauthorized disclosure. • SL 1 – Prevent the unauthorized disclosure of information via eavesdropping or casual exposure. • SL 2 – Prevent the unauthorized disclosure of information to an entity actively searching for it using simple means with low resources, generic skills and low motivation. • SL 3 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with extended resources, IACS specific skills and high motivation. 8.2 Rationale Some control system -generated information, whether at rest or in transit, is of a confidential or sensitive na ture. This implies that some communication channels and data- stores require protection against eavesdr opping and unauthorized access.
SR3.9.1 | SR 3.9 RE (1) | Enhancement | Audit records on write- once media | The control system shall provide the capability to produce audit records on hardware- enforced write -once media. 7.11.3.2 Void | Audit information includes all information (for example, audit records, audit settings and audit reports) needed to successfully audit control system activity. The audit information is important for error correction, security breach recovery, investigations and related efforts. Mechanisms for enhanced protection against modification and deletion include the storage of audit information to hardware- enforced write- once media. | The requirements for the four SL levels that relate to SR 3.9 – Protection of audit information are: • SL-C(SI, control system) 1: Not selected • SL-C(SI, control system) 2: SR 3.9 • SL-C(SI, control system) 3: SR 3.9 • SL-C(SI, control system) 4: SR 3.9 (1) 8 FR 4 – Data confidentiality 8.1 Purpose and SL-C(DC) descriptions Ensure the confidentiality of information on communication channels and in data repositories to prevent unauthorized disclosure. • SL 1 – Prevent the unauthorized disclosure of information via eavesdropping or casual exposure. • SL 2 – Prevent the unauthorized disclosure of information to an entity actively searching for it using simple means with low resources, generic skills and low motivation. • SL 3 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with extended resources, IACS specific skills and high motivation. 8.2 Rationale Some control system -generated information, whether at rest or in transit, is of a confidential or sensitive na ture. This implies that some communication channels and data- stores require protection against eavesdr opping and unauthorized access.
SR4.1 | SR 4.1 | Base requirement | Information confidentiality | The control system shall provide the capability to protect the confidentiality of information for which explicit read authorization is suppor ted, whether at rest or in transit. | Protection of information, at rest or in transit, can be maintained through physical means, compartmentalization or encry ption, among other techniques. It is crucial that the technique chosen consider s the potential ramifications on control system performance and the capability to recover from system failure or attack. The decision whether the confidentiality of a given piece of information should be protected or not depends on the context and cannot be made at product design. However, the fact that an organization limits access to information by configuring explicit read authorizations in the control system is an indicator that this information is considered confidential by the organization. Thus, all information for which the control system supports the capability to assign explicit read authorizations should be considered potentially confidential and thus the control system should also provide the capability to prot ect it. Different organizations and industries may require different levels of encryption strength for different categories of information, based on the sensitivity of the information as well as industry standards and regulatory requirements (see 8.5, SR 4.3 – Use of cryptography). In some situations network configuration information stored and processed in switches and routers may be considered as confidential. Communications involving exposed information transfer may be vulnerable to eavesdropping or tampering. If the control system is depending upon an external commu nications service provider, it may be more difficult to obtain the necessary assurances regarding the implementation of needed security requirements for communication confidentiality. In such cases, it may be appropriate to implement compensating countermeasures or explicitly accept the additional risk. Entities should also be cognizant of information confidentiality when portable and mobile devices are utilized (for example, engineering laptops and USB sticks). As required by 5.7, SR 1.5 – Authenticator management, authentication information, such as passwords, should be considered confidential, and thus never be sent in the clear. | The requirements for the four SL levels that relate to SR 4.1 – Information confidentiality are: • SL-C(DC, control system) 1: SR 4. 1 • SL-C(DC, control system) 2: SR 4. 1 (1) • SL-C(DC, control system) 3: SR 4. 1 (1) • SL-C(DC, control system) 4: SR 4. 1 (1) (2)
SR4.1.1 | SR 4.1 RE (1) | Enhancement | Protection of confidentiality at rest or in transit via untrusted | networks The control system shall provide the capability to protect the confidentiality of i nformation at rest and remote access sessions traversing an untrusted network. NOTE Cryptography is a common mechanism for ensuring information confidentiality. | Protection of information, at rest or in transit, can be maintained through physical means, compartmentalization or encry ption, among other techniques. It is crucial that the technique chosen consider s the potential ramifications on control system performance and the capability to recover from system failure or attack. The decision whether the confidentiality of a given piece of information should be protected or not depends on the context and cannot be made at product design. However, the fact that an organization limits access to information by configuring explicit read authorizations in the control system is an indicator that this information is considered confidential by the organization. Thus, all information for which the control system supports the capability to assign explicit read authorizations should be considered potentially confidential and thus the control system should also provide the capability to prot ect it. Different organizations and industries may require different levels of encryption strength for different categories of information, based on the sensitivity of the information as well as industry standards and regulatory requirements (see 8.5, SR 4.3 – Use of cryptography). In some situations network configuration information stored and processed in switches and routers may be considered as confidential. Communications involving exposed information transfer may be vulnerable to eavesdropping or tampering. If the control system is depending upon an external commu nications service provider, it may be more difficult to obtain the necessary assurances regarding the implementation of needed security requirements for communication confidentiality. In such cases, it may be appropriate to implement compensating countermeasures or explicitly accept the additional risk. Entities should also be cognizant of information confidentiality when portable and mobile devices are utilized (for example, engineering laptops and USB sticks). As required by 5.7, SR 1.5 – Authenticator management, authentication information, such as passwords, should be considered confidential, and thus never be sent in the clear. | The requirements for the four SL levels that relate to SR 4.1 – Information confidentiality are: • SL-C(DC, control system) 1: SR 4. 1 • SL-C(DC, control system) 2: SR 4. 1 (1) • SL-C(DC, control system) 3: SR 4. 1 (1) • SL-C(DC, control system) 4: SR 4. 1 (1) (2)
SR4.1.2 | SR 4.1 RE (2) | Enhancement | Protection of confidentiality across zone boundaries | The control system shall provide the capability to protect the confidentiality of information traversing a ny zone boundar y. | Protection of information, at rest or in transit, can be maintained through physical means, compartmentalization or encry ption, among other techniques. It is crucial that the technique chosen consider s the potential ramifications on control system performance and the capability to recover from system failure or attack. The decision whether the confidentiality of a given piece of information should be protected or not depends on the context and cannot be made at product design. However, the fact that an organization limits access to information by configuring explicit read authorizations in the control system is an indicator that this information is considered confidential by the organization. Thus, all information for which the control system supports the capability to assign explicit read authorizations should be considered potentially confidential and thus the control system should also provide the capability to prot ect it. Different organizations and industries may require different levels of encryption strength for different categories of information, based on the sensitivity of the information as well as industry standards and regulatory requirements (see 8.5, SR 4.3 – Use of cryptography). In some situations network configuration information stored and processed in switches and routers may be considered as confidential. Communications involving exposed information transfer may be vulnerable to eavesdropping or tampering. If the control system is depending upon an external commu nications service provider, it may be more difficult to obtain the necessary assurances regarding the implementation of needed security requirements for communication confidentiality. In such cases, it may be appropriate to implement compensating countermeasures or explicitly accept the additional risk. Entities should also be cognizant of information confidentiality when portable and mobile devices are utilized (for example, engineering laptops and USB sticks). As required by 5.7, SR 1.5 – Authenticator management, authentication information, such as passwords, should be considered confidential, and thus never be sent in the clear. | The requirements for the four SL levels that relate to SR 4.1 – Information confidentiality are: • SL-C(DC, control system) 1: SR 4. 1 • SL-C(DC, control system) 2: SR 4. 1 (1) • SL-C(DC, control system) 3: SR 4. 1 (1) • SL-C(DC, control system) 4: SR 4. 1 (1) (2)
SR4.2 | SR 4.2 | Base requirement | Information persisten ce | The control system shall provide the capability to purge all information for which explicit read authorization is supported from components to be released from active service and/or decommissioned. | Removal of a control system component from active service should not provide the opportunity for unintentional release of information for which explicit read authorization is supported. An example of such information would include ‘join keys’ (in the case of some wireless field devices) stored in non -volatile storage or other cryptographic information that would facilitate unauthorized or malicious activity. Information produced by the actions of a user or role (or the actions of a software process acting on behalf of a user or role) should not be disclosed to a different user or role in an uncontrolled fashion. Control of control system information or data persistence prevents information stored on a shared resource from being unintentionally disclosed after that resource has been released back to the control system. | The requirements for the four SL levels that relate to SR 4.2 – Information persistence are: • SL-C(DC, control system) 1: Not Selected • SL-C(DC, control system) 2: SR 4.2 • SL-C(DC, control system) 3: SR 4.2 (1) • SL-C(DC, control system) 4: SR 4.2 (1)
SR4.2.1 | SR 4.2 RE (1) | Enhancement | Purging of shared memory resources | The control system shall provide the capability to prevent unauthorized and unintended information transfer via volatile shared memory resources. NOTE Volatile memory resources are those that typically do not retain information after being released to memory management. However, there are attacks against random access memory (RAM) that have the potential to extract key material or other confidential data before it is actually over -written. Therefore, it is a commonly accepted practice to purge all unique data and connections to unique data from volatile shared memory when that memory is released back to the control system for use by a different user, such that this data is not visible or accessible to the new user. 8.4.3.2 Void | Removal of a control system component from active service should not provide the opportunity for unintentional release of information for which explicit read authorization is supported. An example of such information would include ‘join keys’ (in the case of some wireless field devices) stored in non -volatile storage or other cryptographic information that would facilitate unauthorized or malicious activity. Information produced by the actions of a user or role (or the actions of a software process acting on behalf of a user or role) should not be disclosed to a different user or role in an uncontrolled fashion. Control of control system information or data persistence prevents information stored on a shared resource from being unintentionally disclosed after that resource has been released back to the control system. | The requirements for the four SL levels that relate to SR 4.2 – Information persistence are: • SL-C(DC, control system) 1: Not Selected • SL-C(DC, control system) 2: SR 4.2 • SL-C(DC, control system) 3: SR 4.2 (1) • SL-C(DC, control system) 4: SR 4.2 (1)
SR4.3 | SR 4.3 | Base requirement | Use of cryptography | If cryptogr aphy is required, the control system shall use cryptographic algorithms, key sizes and mechanisms for key establishment and management according to commonly accepted security industry practices and recommendations. | The selection of cryptographic protection should match the value of the information being protected, the consequences of the confidentiality of the information being breached, the time period during which the information is confidential and control system operating constraints. This can involve either information at rest, in transit, or both. Note that backups are an example of information at rest, and should be considered as part of a data confidentiality assessment process. The control system product supp lier should document the practices and procedures relating to cryptographic key establishment and management. The control system should utilize established and tested encryption and hash algorithm s, such as the advanced encryption standard (AES) and the secure hash algorithm (SHA) series, and key sizes based on an assigned standard. Key generation needs to be performed using an effective random number generator. The security policies and procedures for key management need to address period ic key changes, ke y destruction, key distribution and encryption key backup in accordance with defined standards. Generally accepted practices and recommendations can be found in documents such as NIST SP800- 57 [25]. Implementation requirements can be found for example in ISO/IEC 19790 [12]. This SR, along with 5.10, SR 1.8 – Public key infrastructure (PKI) certificates may be applicable when meeting many other requirements defined within this standard. | The requirements for the four SL levels that relate to SR 4.3 – Use of cryptography are: • SL-C(DC, control system) 1: SR 4.3 • SL-C(DC, control system) 2: SR 4.3 • SL-C(DC, control system) 3: SR 4.3 • SL-C(DC, control system) 4: SR 4.3 9 FR 5 – Restrict ed data flow 9.1 Purpose and SL-C(RDF) descriptions Segment the control system via zones and conduits to limi t the unnecessary flow of data. • SL 1 – Prevent the casual or coincidental circumvention of zone and conduit segmentation. • SL 2 – Prevent the intended circumvention of zone and conduit segmentation by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Prevent the intended circumvention of zone and conduit segmentation by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation. • SL 4 – Prevent the intended circumvention of zone and conduit segmentation by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 9.2 Rationale Using their risk assessment methodology, asset owners need to determine necessary information flow restrictions and thus, by extension, determine the configuration of the condui ts used to deliver this information. Derived prescriptive recommendations and guidelines should include mechanisms that range from disconnecting control system networks from business or public networks to using unidirectional gateways, stateful firewalls and DMZs to manage the flow of information.
SR5.1 | SR 5.1 | Base requirement | Network segmentation | The control system shall provide the capability to logically segment control system networks from non- control system networks and to lo gically segment critical control system networks from other control system networks. | Network segmentation is used by organizations for a variety of purposes, including cyber security. The main reasons for segmenting networks are to reduce the exposure, or ingress, of network traffic into a control system and reduce the spread, or egress, of network traffic from a control system. This improves overall system response and reliability as well as provides a measure of cyber security protection. It also allows different network segments within the control system, including critical control systems and safety -related systems, to be segmented from other systems for an additional level of protection. Access from the control system to the World Wide Web should be clearly justified based on control system operational requirements. Network segmentation and the level of protection it provides will vary greatly d epending on the overall network architecture used by an asset owner in their facility and even system integrators within their control systems. Logically segmenting networks based on their functionality provides some measure of protection, but may still lead to single- points -of-failure if a network device is compromised. Physically segmenting networks provides another level of protection by removing that single- point -of-failure case, but will lead to a more complex and costly network design. These trade- offs will need to be evaluated during the network design process (see IEC 62443‑2‑1). In response to an incident, it may be necessary to break the connections between different network segments. In that event, the services necessary to support essential operations should be maintained in such a way that the devices can continue to operate properly and/or shutdown in an orderly manner. This may require that some servers may need to be duplicated on the control system network to support normal network features, for example dynamic host configuration protocol (DHCP), domain name service (DNS) or local CAs. It may also mean that some critical control systems and safety -related systems be designed from the beginning to be completely isolated from other networks. | The requirements for the four SL levels that relate to SR 5. 1 – Network segmentation are: • SL-C(RDF, control system) 1: SR 5. 1 • SL-C(RDF, control system) 2: SR 5. 1 (1) • SL-C(RDF, control system) 3: SR 5. 1 (1) (2) • SL-C(RDF, control system) 4: SR 5. 1 (1) (2) (3)
SR5.1.1 | SR 5.1 RE (1) | Enhancement | Physical network segmentation | The control system shall provide the capability to physically segment control sys tem networks from non- control system networks and to physically segment critical control system networks from non- critical control system networks. | Network segmentation is used by organizations for a variety of purposes, including cyber security. The main reasons for segmenting networks are to reduce the exposure, or ingress, of network traffic into a control system and reduce the spread, or egress, of network traffic from a control system. This improves overall system response and reliability as well as provides a measure of cyber security protection. It also allows different network segments within the control system, including critical control systems and safety -related systems, to be segmented from other systems for an additional level of protection. Access from the control system to the World Wide Web should be clearly justified based on control system operational requirements. Network segmentation and the level of protection it provides will vary greatly d epending on the overall network architecture used by an asset owner in their facility and even system integrators within their control systems. Logically segmenting networks based on their functionality provides some measure of protection, but may still lead to single- points -of-failure if a network device is compromised. Physically segmenting networks provides another level of protection by removing that single- point -of-failure case, but will lead to a more complex and costly network design. These trade- offs will need to be evaluated during the network design process (see IEC 62443‑2‑1). In response to an incident, it may be necessary to break the connections between different network segments. In that event, the services necessary to support essential operations should be maintained in such a way that the devices can continue to operate properly and/or shutdown in an orderly manner. This may require that some servers may need to be duplicated on the control system network to support normal network features, for example dynamic host configuration protocol (DHCP), domain name service (DNS) or local CAs. It may also mean that some critical control systems and safety -related systems be designed from the beginning to be completely isolated from other networks. | The requirements for the four SL levels that relate to SR 5. 1 – Network segmentation are: • SL-C(RDF, control system) 1: SR 5. 1 • SL-C(RDF, control system) 2: SR 5. 1 (1) • SL-C(RDF, control system) 3: SR 5. 1 (1) (2) • SL-C(RDF, control system) 4: SR 5. 1 (1) (2) (3)
SR5.1.2 | SR 5.1 RE (2) | Enhancement | Independence from non -control system networks | The control system shall have the capability to provide network services to control system networks, critical or otherwise, without a connection to non- control system networks. | Network segmentation is used by organizations for a variety of purposes, including cyber security. The main reasons for segmenting networks are to reduce the exposure, or ingress, of network traffic into a control system and reduce the spread, or egress, of network traffic from a control system. This improves overall system response and reliability as well as provides a measure of cyber security protection. It also allows different network segments within the control system, including critical control systems and safety -related systems, to be segmented from other systems for an additional level of protection. Access from the control system to the World Wide Web should be clearly justified based on control system operational requirements. Network segmentation and the level of protection it provides will vary greatly d epending on the overall network architecture used by an asset owner in their facility and even system integrators within their control systems. Logically segmenting networks based on their functionality provides some measure of protection, but may still lead to single- points -of-failure if a network device is compromised. Physically segmenting networks provides another level of protection by removing that single- point -of-failure case, but will lead to a more complex and costly network design. These trade- offs will need to be evaluated during the network design process (see IEC 62443‑2‑1). In response to an incident, it may be necessary to break the connections between different network segments. In that event, the services necessary to support essential operations should be maintained in such a way that the devices can continue to operate properly and/or shutdown in an orderly manner. This may require that some servers may need to be duplicated on the control system network to support normal network features, for example dynamic host configuration protocol (DHCP), domain name service (DNS) or local CAs. It may also mean that some critical control systems and safety -related systems be designed from the beginning to be completely isolated from other networks. | The requirements for the four SL levels that relate to SR 5. 1 – Network segmentation are: • SL-C(RDF, control system) 1: SR 5. 1 • SL-C(RDF, control system) 2: SR 5. 1 (1) • SL-C(RDF, control system) 3: SR 5. 1 (1) (2) • SL-C(RDF, control system) 4: SR 5. 1 (1) (2) (3)
SR5.1.3 | SR 5.1 RE (3) | Enhancement | Logical and physical isolation of critical networks | The control system shall provide the capability to logically and physically isolate critical control system networks from non- critical control system networks. | Network segmentation is used by organizations for a variety of purposes, including cyber security. The main reasons for segmenting networks are to reduce the exposure, or ingress, of network traffic into a control system and reduce the spread, or egress, of network traffic from a control system. This improves overall system response and reliability as well as provides a measure of cyber security protection. It also allows different network segments within the control system, including critical control systems and safety -related systems, to be segmented from other systems for an additional level of protection. Access from the control system to the World Wide Web should be clearly justified based on control system operational requirements. Network segmentation and the level of protection it provides will vary greatly d epending on the overall network architecture used by an asset owner in their facility and even system integrators within their control systems. Logically segmenting networks based on their functionality provides some measure of protection, but may still lead to single- points -of-failure if a network device is compromised. Physically segmenting networks provides another level of protection by removing that single- point -of-failure case, but will lead to a more complex and costly network design. These trade- offs will need to be evaluated during the network design process (see IEC 62443‑2‑1). In response to an incident, it may be necessary to break the connections between different network segments. In that event, the services necessary to support essential operations should be maintained in such a way that the devices can continue to operate properly and/or shutdown in an orderly manner. This may require that some servers may need to be duplicated on the control system network to support normal network features, for example dynamic host configuration protocol (DHCP), domain name service (DNS) or local CAs. It may also mean that some critical control systems and safety -related systems be designed from the beginning to be completely isolated from other networks. | The requirements for the four SL levels that relate to SR 5. 1 – Network segmentation are: • SL-C(RDF, control system) 1: SR 5. 1 • SL-C(RDF, control system) 2: SR 5. 1 (1) • SL-C(RDF, control system) 3: SR 5. 1 (1) (2) • SL-C(RDF, control system) 4: SR 5. 1 (1) (2) (3)
SR5.3 | SR 5.3 | Base requirement | General purpose person -to-person communication restrictions | The control system shall provide the capability to prevent general purpose person -to-person messages from being received from users or systems external to the control system. | General purpose person -to-person communications systems include but are not limited to: email systems, forms of social media (Twitter, Facebook, picture galleries, etc.) or any message systems that permit the transmission of any type of executable file. These systems are usually utilized for private purposes which are not related to control system operations, and therefore the risks imposed by these system s normally outweigh any perceived benefit. These types of general purpose communications systems are commonly used attack vectors to introduce malware to the control system, pass information for which read authorization exists to locations external to the control system, and introduce excessive netw ork loading that can be used to create security problems or launch attacks on the control system. Application of a broad range of other system requirements covering, for example, usage restrictions and limiting data flow as described elsewhere in this standard to general purpose person- to-person communication systems can provide adequate compensating countermeasures to meet this requirement. The control system may provide the capability to utilize these types of two- way communication systems, but only betwe en servers and/or workstations within the control system. Note that this SR needs to support the requirements associated with 8.3, SR 4.1 – Information confidentiality. The control system may also restrict email or other messaging solutions that provide internal computer -to-external computer communications using outbound messages. These internal -toexternal communications may be limited to the purpose of sending system alerts or other computer generated information messages to users or systems external to the control system. To prevent the passing of information for which explicit read authorization is supported, pre - configured messages (perhaps with the ability to include some limited text) should be used to transmit the alerts or status information. Users may not be given the ability to attach files or other information t o these outbound- only messages at the time the messages are created by the system. | The requirements for the four SL levels that relate to SR 5.3 – General purpose person -toperson communication restrictions are: • SL-C(RDF, control system) 1: SR 5.3 • SL-C(RDF, control system) 2: SR 5.3 • SL-C(RDF, control system) 3: SR 5.3 (1) • SL-C(RDF, control system) 4: SR 5.3 (1)
SR5.3.1 | SR 5.3 RE (1) | Enhancement | Prohibit all general purpose person- to-person communications | The control system shall provide the capability to prevent both transmiss ion and receipt of general purpose person- to-person messages. 9.5.3.2 Void | General purpose person -to-person communications systems include but are not limited to: email systems, forms of social media (Twitter, Facebook, picture galleries, etc.) or any message systems that permit the transmission of any type of executable file. These systems are usually utilized for private purposes which are not related to control system operations, and therefore the risks imposed by these system s normally outweigh any perceived benefit. These types of general purpose communications systems are commonly used attack vectors to introduce malware to the control system, pass information for which read authorization exists to locations external to the control system, and introduce excessive netw ork loading that can be used to create security problems or launch attacks on the control system. Application of a broad range of other system requirements covering, for example, usage restrictions and limiting data flow as described elsewhere in this standard to general purpose person- to-person communication systems can provide adequate compensating countermeasures to meet this requirement. The control system may provide the capability to utilize these types of two- way communication systems, but only betwe en servers and/or workstations within the control system. Note that this SR needs to support the requirements associated with 8.3, SR 4.1 – Information confidentiality. The control system may also restrict email or other messaging solutions that provide internal computer -to-external computer communications using outbound messages. These internal -toexternal communications may be limited to the purpose of sending system alerts or other computer generated information messages to users or systems external to the control system. To prevent the passing of information for which explicit read authorization is supported, pre - configured messages (perhaps with the ability to include some limited text) should be used to transmit the alerts or status information. Users may not be given the ability to attach files or other information t o these outbound- only messages at the time the messages are created by the system. | The requirements for the four SL levels that relate to SR 5.3 – General purpose person -toperson communication restrictions are: • SL-C(RDF, control system) 1: SR 5.3 • SL-C(RDF, control system) 2: SR 5.3 • SL-C(RDF, control system) 3: SR 5.3 (1) • SL-C(RDF, control system) 4: SR 5.3 (1)
SR5.4 | SR 5.4 | Base requirement | Application partitioning | The control system shall provide the capability to support partitioning of data, applications and services based on criticality to facilitate implementing a zoning model. | Partitioning may be accomplished via physical or logi cal means through the use of different computers, different central processing units, different instances of the operating system, different network addresses and combinations of these methods or other methods as appropriate. Examples of applications and services that could be considered for different partitions include, but are not limited to, emergency and/or safety systems, closed- loop control applications, operator workstations and engineering workstations. | The requirements for the four SL levels that relate to SR 5.4 – Application partitioning are: • SL-C(RDF, control system) 1: SR 5.4 • SL-C(RDF, control system) 2: SR 5. 4 • SL-C(RDF, control system) 3: SR 5.4 • SL-C(RDF, control system) 4: SR 5.4 10 FR 6 – Timely response to event s 10.1 Purpose and SL-C(TRE) descriptions Respond to security violations by notifying the proper authority, reporting needed evidence of the violation and taking timely corrective action when incidents are discovered. • SL 1 – Monitor the operation of the IACS and respond to incidents when they are discovered by collecting and providing the forensic evidence when queried. • SL 2 – Monitor the operation of t he IACS and respond to incidents when they are discovered by actively collecting and periodically reporting forensic evidence. • SL 3 – Monitor the operation of the IACS and respond to incidents when they are discovered by actively collecting and pushing forensic evidence to the proper authority. • SL 4 – Monitor the operation of the IACS and respond to incidents when they are discovered by actively collecting and pushing forensic evidence to the proper authority in near real -time. 10.2 Rationale Using their risk as sessment methodology, asset owners should establish security policies and procedures and proper lines of communication and control needed to r espond to security violations. Derived prescriptive recommendations and guidelines should include mechanisms that collect, report, preserve and automatically correlate the forensic evidence to ensure timely corrective action. The use of monitoring tools and techniques should not adversely affect the operational performance of the control system.
SR6.1 | SR 6.1 | Base requirement | Audit log acc essibility | The control system shall provide the capability for authorized humans and/or tools to access audit logs on a read -only basis. | The control system generates audit records about events occurring in the system (see 6.10, SR 2.8 – Auditable events). Access to these audit log s is necessary to support filtering audit logs, identifying and removing information that is redundant, review ing and reporting activity during after -the-fact investigations of security incidents. This access should not alter the original audit records. In general, audit reduction and report generation should be performed on a separate information system. Manual access to the audit records (such as screen views or printouts) is sufficient for meeting the base requirement, but is insufficient for higher SLs. Programmatic access is commonly used to provide the audit log information to analysis mechanisms such as SIEM. See relevant SRs in Clauses 5, 6 and 9 regarding the creation of, protection of and access to audit logs. | The requirements for the four SL levels that relate to SR 6.1 – Audit log accessibility are: • SL-C(TRE, control system) 1: SR 6.1 • SL-C(TRE, control system) 2: SR 6.1 • SL-C(TRE, control system) 3: SR 6.1 (1) • SL-C(TRE, control system) 4: SR 6.1 (1)
SR6.1.1 | SR 6.1 RE (1) | Enhancement | Programmatic access to audit logs | The control system shall provide programmatic access to audit records using an application programming interface (API). 10.3.3.2 Void | The control system generates audit records about events occurring in the system (see 6.10, SR 2.8 – Auditable events). Access to these audit log s is necessary to support filtering audit logs, identifying and removing information that is redundant, review ing and reporting activity during after -the-fact investigations of security incidents. This access should not alter the original audit records. In general, audit reduction and report generation should be performed on a separate information system. Manual access to the audit records (such as screen views or printouts) is sufficient for meeting the base requirement, but is insufficient for higher SLs. Programmatic access is commonly used to provide the audit log information to analysis mechanisms such as SIEM. See relevant SRs in Clauses 5, 6 and 9 regarding the creation of, protection of and access to audit logs. | The requirements for the four SL levels that relate to SR 6.1 – Audit log accessibility are: • SL-C(TRE, control system) 1: SR 6.1 • SL-C(TRE, control system) 2: SR 6.1 • SL-C(TRE, control system) 3: SR 6.1 (1) • SL-C(TRE, control system) 4: SR 6.1 (1)
SR6.2 | SR 6.2 | Base requirement | Continuous monitoring | The control system shall provide the capability to continuously monitor all security mechanism performance using commonly accepted security industry practices and recommendations to detect, characterize and report security breaches in a timely manner. NOTE Response time is a local matter outside the scope of this standard. | Control system monitoring capability can be achieved through a variety of tools and techniques (for exam ple, IDS, IPS, malicious code protection mechanisms and network monitoring mechanisms). As attacks become more sophisticated, these monitoring tools and techniques will need to become more sophisticated as well, including for example behavior - based IDS/IPS. Monitoring devices should be strategically deployed within the control system (for example, at selected perimeter locations and near server farms supporting critical applications) to collect essential inf ormation. Monitoring mechanisms may also be deploy ed at ad hoc locations within the control system t o track specific transactions. Monitoring should include appropriate reporting mechanisms to allow for a timely response to events. To keep the reporting focused and the amount of reported information to a level that can be processed by the recipients, mechanisms such as SIEM are commonly applied to correlate individual events into aggregate reports which establish a larger context in which the raw events occurred. Additionally, these mechanisms can be used to track the effect of security changes to the control system (see 6.10, SR 2.8 – Auditable events). Having forensic tools pre -installed can facilitate incident analysis. | The requirements for the four SL levels that relate to SR 6.2 – Continuous monitoring are: • SL-C(TRE, control system) 1: Not Selected • SL-C(TRE, control system) 2: SR 6.2 • SL-C(TRE, control system) 3: SR 6.2 • SL-C(TRE, control system) 4: SR 6.2 11 FR 7 – Resource avail ability 11.1 Purpose and SL-C(RA) descriptions Ensure the availability of the control system against th e degradation or denial of essential services. • SL 1 – Ensure that the control system operates reliably under normal production conditions and prevents DoS situations caused by the casual or coincidental actions of an entity. • SL 2 – Ensure that the control system operates reliably under normal and abnormal production conditions and prevents DoS situations by entities using simple means with low resources, generic skills and low motivation. • SL 3 – Ensure that the control system operates reliably under normal, abnormal, and extreme production conditions and prevents DoS situations by entities using sophisticated means with moderate resour ces, IACS specific skills and moderate motivation. • SL 4 – Ensure that the control system operates reliably under normal, abnormal, and extreme production conditions and prevents DoS situations by entities using sophisticated means with extended resources, IACS specific skills and high motivation. 11.2 Rationale The aim of this series of SRs is to ensure that the control system is resilient against various types of DoS events. This includes the partial or total unavailability of system functionality at various le vels. In particular, security incidents in the control system should not affect SIS or other safety -related functions.
SR7.1 | SR 7.1 | Base requirement | Denial of service protection | The control system shall provide the capability to operate in a degraded mode during a DoS event. | A variety of technologies exist to limit, or in some cases, eliminate the effects of DoS situations. For example, boundary protection devices can filter certain types of packets to protect devices on an intern al, trusted network from being directly affected by DoS events or restricting the information flow to be unidirectional outbound. Specifically, as noted in Clause 4, a DoS event on the control system should not adversely impact any safety -related systems. | The requirements for the four SL levels that relate to SR 7.1 – Denial of service protection are: • SL-C(RA, control system) 1: SR 7.1 • SL-C(RA, control system) 2: SR 7.1 (1) • SL-C(RA, control system) 3: SR 7.1 (1) (2) • SL-C(RA, control system) 4: SR 7.1 (1) (2)
SR7.1.1 | SR 7.1 RE (1) | Enhancement | Manage communication loads | The control system shall provide the capability to manage communication loads (such as using rate limiting) to mitigate the effects of information flooding types of DoS events. | A variety of technologies exist to limit, or in some cases, eliminate the effects of DoS situations. For example, boundary protection devices can filter certain types of packets to protect devices on an intern al, trusted network from being directly affected by DoS events or restricting the information flow to be unidirectional outbound. Specifically, as noted in Clause 4, a DoS event on the control system should not adversely impact any safety -related systems. | The requirements for the four SL levels that relate to SR 7.1 – Denial of service protection are: • SL-C(RA, control system) 1: SR 7.1 • SL-C(RA, control system) 2: SR 7.1 (1) • SL-C(RA, control system) 3: SR 7.1 (1) (2) • SL-C(RA, control system) 4: SR 7.1 (1) (2)
SR7.1.2 | SR 7.1 RE (2) | Enhancement | Limit DoS effects to other systems or networks | The control system shall provide the capability to restrict the ability of all users (humans, software processes and devices) to cause DoS events which affect other control systems or networks. | A variety of technologies exist to limit, or in some cases, eliminate the effects of DoS situations. For example, boundary protection devices can filter certain types of packets to protect devices on an intern al, trusted network from being directly affected by DoS events or restricting the information flow to be unidirectional outbound. Specifically, as noted in Clause 4, a DoS event on the control system should not adversely impact any safety -related systems. | The requirements for the four SL levels that relate to SR 7.1 – Denial of service protection are: • SL-C(RA, control system) 1: SR 7.1 • SL-C(RA, control system) 2: SR 7.1 (1) • SL-C(RA, control system) 3: SR 7.1 (1) (2) • SL-C(RA, control system) 4: SR 7.1 (1) (2)
SR7.2 | SR 7.2 | Base requirement | Resource m anagement | The control system shall provide the capability to limit the use of resources by security functions to prevent resource exhaustion. | Resource management (for example, network segmentation or priority schemes) prevent s a lower -priority software process from delaying or interfering with the control system servicing any higher -priority software process. For example, initiating network scans, patching and/or antivirus checks on an operating system can cause severe disruption to normal operations. Traffic rate limiting schemes should be considered as a mitiga tion technique. | The requirements for the four SL levels that relate to SR 7.2 – Resource management are: • SL-C(RA, contr ol system) 1: SR 7.2 • SL-C(RA, control system) 2: SR 7.2 • SL-C(RA, control system) 3: SR 7.2 • SL-C(RA, control system) 4: SR 7.2
SR7.3 | SR 7.3 | Base requirement | Control system backup | The identity and location of critical files and the ability to conduct backups of user -level and system -level information (including system state information) shall be supported by the control system without affe cting normal plant operations. | The a vailability of up -to-date backups is essential for recovery from a control system failure and/or mis-configuration. Automating this function ensures that all required files are captured, reducing operator overhead. Although not usually requir ed for control system recovery, information required for post -incident forensic activity (for example, audit logs) should be specifically included in the backup (see 10.4, SR 6.2 – Continuous monitoring). If the resulting backups contain confidential information, encryption should be considered (see 8.5, SR 4.3 – Use of cryptography). | The requirements for the four SL levels that relate to SR 7.3 – Control system backup are: • SL-C(RA, control system) 1: SR 7.3 • SL-C(RA, control system) 2: SR 7.3 (1) • SL-C(RA, control system) 3: SR 7.3 (1) (2) • SL-C(RA, control system) 4: SR 7.3 (1) (2)
SR7.3.1 | SR 7.3 RE (1) | Enhancement | Backup verification | The control system shall provide the capability to verify the reliability of backup mechanisms. | The a vailability of up -to-date backups is essential for recovery from a control system failure and/or mis-configuration. Automating this function ensures that all required files are captured, reducing operator overhead. Although not usually requir ed for control system recovery, information required for post -incident forensic activity (for example, audit logs) should be specifically included in the backup (see 10.4, SR 6.2 – Continuous monitoring). If the resulting backups contain confidential information, encryption should be considered (see 8.5, SR 4.3 – Use of cryptography). | The requirements for the four SL levels that relate to SR 7.3 – Control system backup are: • SL-C(RA, control system) 1: SR 7.3 • SL-C(RA, control system) 2: SR 7.3 (1) • SL-C(RA, control system) 3: SR 7.3 (1) (2) • SL-C(RA, control system) 4: SR 7.3 (1) (2)
SR7.3.2 | SR 7.3 RE (2) | Enhancement | Backup automation | The control system shall provide the capability to automate the backup function based on a configurable frequency. | The a vailability of up -to-date backups is essential for recovery from a control system failure and/or mis-configuration. Automating this function ensures that all required files are captured, reducing operator overhead. Although not usually requir ed for control system recovery, information required for post -incident forensic activity (for example, audit logs) should be specifically included in the backup (see 10.4, SR 6.2 – Continuous monitoring). If the resulting backups contain confidential information, encryption should be considered (see 8.5, SR 4.3 – Use of cryptography). | The requirements for the four SL levels that relate to SR 7.3 – Control system backup are: • SL-C(RA, control system) 1: SR 7.3 • SL-C(RA, control system) 2: SR 7.3 (1) • SL-C(RA, control system) 3: SR 7.3 (1) (2) • SL-C(RA, control system) 4: SR 7.3 (1) (2)
SR7.4 | SR 7.4 | Base requirement | Control system recovery and reconstitution | The control system shall provide the capability to recover and reconstitut e to a known secure state afte r a disruption or failure. | Control system recovery and reconstitution to a known secure state means that all system parameters (either default or configurable) are set to secure values, security -critical patches are reinstalled, security -related configuration settings are reestablished, system documentation and operating procedures are available, application and system software is reinstalled and configured with secure settings, information from the most recent, known secure backups is loaded and the system is fully tested and functional. | The requirements for the four SL levels that relate to SR 7.4 – Control system recovery and reconstitution are: • SL-C(RA, control system) 1: SR 7.4 • SL-C(RA, control system) 2: SR 7.4 • SL-C(RA, control system) 3: SR 7.4 • SL-C(RA, control system) 4: SR 7.4
SR7.5 | SR 7.5 | Base requirement | Emergency power | The control system shall provide the capability to switch to and from an emergency power supply without affecting the existing security state or a documented degraded mode. | There may be instances where compensating countermeasures s uch as physical door access control may be affected by loss of base power supply, in which case the emergency power supply should cover those associated systems. If this is not possible, other compensating countermeasures may be needed during such an emergency situation. | The requirements for the four SL levels that relate to SR 7.5 – Emergency power are: • SL-C(RA, control s ystem) 1: SR 7.5 • SL-C(RA, control system) 2: SR 7.5 • SL-C(RA, control system) 3: SR 7.5 • SL-C(RA, control system) 4: SR 7.5
SR7.6 | SR 7.6 | Base requirement | Network and security configuration settings | The control system shall provide the capability to be configured according to recommended network and security configurations as described in guidelines provided by the control system supplier. The control system shall provide an interface to the currently deployed network and security configuration settings. | These configuration settings are the adjustable parameters of the control system components. In order to be able to detect and correct any deviations from the approved and/or recommended configuration settings, the control system needs to support monitoring and control of changes to the configuration settings in accordance with security policies and procedures. For enhanced security, an automated check may be performed where the current settings are automatically collected by an agent and compared to approved settings. | The requirements for the four SL levels that relate to SR 7.6 – Network and security configuration settings are: • SL-C(RA, control system) 1: SR 7.6 • SL-C(RA, control system) 2: SR 7.6 • SL-C(RA, control system) 3: SR 7.6 (1) • SL-C(RA, control system) 4: SR 7.6 (1)
SR7.6.1 | SR 7.6 RE (1) | Enhancement | Machine- readable reporting of current security settings | The control system shall provide the capability to generate a report listing the currently deployed security settings in a machine -readable format. 11.8.3.2 Void | These configuration settings are the adjustable parameters of the control system components. In order to be able to detect and correct any deviations from the approved and/or recommended configuration settings, the control system needs to support monitoring and control of changes to the configuration settings in accordance with security policies and procedures. For enhanced security, an automated check may be performed where the current settings are automatically collected by an agent and compared to approved settings. | The requirements for the four SL levels that relate to SR 7.6 – Network and security configuration settings are: • SL-C(RA, control system) 1: SR 7.6 • SL-C(RA, control system) 2: SR 7.6 • SL-C(RA, control system) 3: SR 7.6 (1) • SL-C(RA, control system) 4: SR 7.6 (1)
SR7.7 | SR 7.7 | Base requirement | Least functionality | The control system shall provide the capability to specifically prohibit and/or restrict the use of unnecessary functions, ports, protocols and/or services. | Control systems are capable of providing a wide var iety of functions and services. Some of the functions and services provided may not be necessary to support essential func tions. Therefore, by default, functions beyond a baseline configuration should be disabled. Additionally, it is sometimes convenient t o provide multiple services from a single component of a control system, but doing so increases risk over limiting the services provided by any one component. Many functions and services commonly provided by commercial -off-the-shelf (COTS) equipment may be candidates for elimination, for example, email, voice over internet protocol (VoIP), instant messaging (IM), file transfer protocol (FTP), hypertext transfer protocol (HTTP) and file sharing. | The requirements for the four SL levels that relate to SR 7.7 – Least functionality are: • SL-C(RA, control system) 1: SR 7.7 • SL-C(RA, control system) 2: SR 7.7 • SL-C(RA, control system) 3: SR 7.7 • SL-C(RA, control system) 4: SR 7.7
SR7.8 | SR 7.8 | Base requirement | Control system component inventory | The control system shall provide the cap ability to report the current list of installed components and their associated properties. | A control system component inventory may include but is not limited to component ID, capability and revision level. The component inventory should be consistent with the SuC. A formal process of configuration management should be deployed to keep control of the changes in the component inventory baseline (see IEC 62443‑2‑1). | The requirements for the four SL levels that relate to SR 7.8 – Control system component inventory are: • SL-C(RA, control system) 1: Not Selected • SL-C(RA, control system) 2: SR 7.8 • SL-C(RA, control system) 3: SR 7.8 • SL-C(RA, control system) 4: SR 7.8 Annex A (informative) Discussion of the SL vector NOTE 1 This annex is based on the paper titled “ Security Assurance Levels: A Vector Approach to Describing Security Requirements ” [28]. The content in this annex has been modified from that original paper to respond to changes in the IEC 62443 series and comments received from reviewers. NOTE 2 The ulti mate home for the majority of the material contained in this annex will be IEC 62443‑1‑1 and IEC 62443‑ 3‑2. At the time of this documents publication, these other documents were being written and/or revised and did not contain the material on the SL vector. This annex has been provided to aid the reader in understanding the SL vector concept. The material in this annex is informative and will be superseded by any normative content included in those other standards. A.1 Overview Safety systems have used the concept of safety integrity levels (SILs) for almost two decades. This allows the safety integrity capability of a component or the safety integrity level of a deployed system to be represented by a single number that defines a protection factor required to ensure the health and safety of people or the environment based on the probability of failure of that component or system. The process to determine the required prot ection factor for a safety system, while complex, is manageable since the probability of a component or system failure due to random hardware failures can be measured in quantitative terms. The overall risk can be calculated based on the consequences that those failures could potentially have on HSE. Security systems have much broader application, a much broader set of consequences and a much broader set of possible circumstances leading up to a possible event. Security systems are still meant to protect HS E, but they are also meant to protect the industrial process itself, company -proprietary information, public confidence and national security among other things in situations where random hardware failures may not be the root cause. In some cases, it may b e a well -meaning employee that makes a mistake, and in other cases it may be a devious attacker bent on causing an event and hiding the evidence. The increased complexity of security systems makes compressing the protection factor down to a single number m uch more difficult. A.2 Security levels A.2.1 Definition The following is an excerpt from 5.11.1 of IEC/TS 62443‑1‑1:2009 that provides a good explanation of what SLs are and how they can be used. Security levels provide a qualitative approach to addressing security for a zone. As a qualitative method, security level definition has applicability for comparing and managing the security of zones within an organization. As more data becomes available and the mathematical repres entations of risk, threats, and security incidents are developed, this concept will move to a quantitative approach for selection and verification of Security Levels (SL). It will have applicability to both end user companies, and vendors of IACS and security products. It will be used to select IACS devices and countermeasures to be used within a zone and to identify and compare security of zones in different organizations across industry segments. In the first phase of development, the IEC 62443 series of standards tends to use qualitative SLs, using terms such as “low”, “medium”, and “high”. The asset owner will be required to come up with their own definition of what those classifications mean for their particul ar application. The long -term goal for the IEC 62443 series is to move as many of the security levels and requirements to quantita tive descriptions, requirements and metrics as possible to establish repeatable applications of the standard across multiple companies and industries. Achieving this goal will take time, since more experience in applying the standards and data on industrial security systems will need to be acquired to justify the quantitative approach. When mapping requirements to the different SLs, standard developers need some frame of reference describing what the different SLs mean and how they differ from each other. The goal of this annex is to propose such a frame of reference. A.2.2 Types of SLs SLs have been broken down into three different types: target, achieved and capabilit y. These types, while they all are related have to do with different aspects of the security lifecycle. • Target SLs (SL-T) are the desired level of security for a particular system. This is usually determined by performing a risk assessment on a system and determining that it needs a particular level of security to ensure its correct operation. • Achieved SLs (SL-A) are the actual level of security for a particular system. Thes e are measured after a system design is available or when a system is in place. They are used to establish that a security system is meeting the goals that were originally set out in the target SLs. • Capability SLs (SL-C) are the security levels that compon ents or systems can provide when properly configured. These levels state that a particular component or system is capable of meeting the target SLs natively without additional compensating countermeasures when properly configured and integrated. Each of these SLs is intended to be used in differ ent phases of the security lifecycle according the IEC 62443 series. Starting with a target for a particular system, an organization would need to build a design that included the capabilities to achieve the desired result. In other words, the design team would first develop the target SL necessary for a particular system. They would then design the system to meet those targets, usually in an iterative process where after each iteration the achieved SLs of the proposed design are measured and compared to the target SLs. As part of that design process, the designers would select components and systems with the necessary capability SLs to meet the target SL requirements – or wh ere such systems and components are not available, complement the available ones with compensating countermeasures. After the system went into operation, the actual SL would be measured as the achieved SL and compared to the target SL. A.2.3 Using SLs When designing a new system (green field) or revising the security of an existing system (brown field), the first step is to break the system into different zones and define conduits connecting these zones where necessary. Details on how to accomplish this are given in IEC 62443‑3‑2. Once a zone model of the system is established each zone and conduit is assigned a target SL, based on a consequence analysis, which describes the desired security for the respective zone or conduit. During this initial zone and conduit analysis, it is not necessary to have completed a detailed system design. It is sufficient to describe the functionality that should be provided by assets in a zone and the connections between zones in order to meet the security objectives. Figure A. 1 and Figure A. 2 show high -level examples of systems broken down into zones connected by conduits. Figure A. 1 is a graphical representation of a control system for a chlorine truck loading station. The full use- case that accompanies this figure will be discussed in IEC/TR 62443‑1‑4. It has five zones shown: the basic process control system (BPCS), the SIS, the control center, the plant DMZ, and the enterpri se. The BPCS and SIS both use PLCs to operate different aspects of the loading station with the SIS using a special functional safety PLC (FS -PLC) rated for use in safety systems. The two PLCs are connected via a nonroutable serial or Ethernet connection using a boundary protection device. Each of the PLCs is connected to a local switch with an engineering workstation for programming and HMI for operating. The BPCS and SIS zone s also contain an instrument asset management system (IAMS) to measure and test the instruments. A control center containing multiple workstations and the BPCS are both connected to the plant DMZ. A plant DMZ can house a variety of components and systems, for example a data historian and a maintenance workstation as shown in the figure. The plant DMZ is shown connected to the enterprise systems, which contain the corporate wireless local area network (WLAN) and web server. Multiple domain controllers and boundary protection devices are shown in the figure to indicate some of the count ermeasures that may be applied to improve security. Figure A.1 – High -level process- industry example showing zones and conduits Figure A. 2 is a graphical representation of a manufacturing plant. It has four zones defined: the enterprise network, the industrial/enterprise DMZ, and two industrial networks. The enterprise infrastructure has a WLAN and a connection to the Int ernet. Many companies use a DMZ between important parts of their systems to isolate the network traffic. In this particular example, each industrial network operates relatively independent of each other with its own PLC, field devices, and HMI. IEC 2032/13 Figure A.2 – High -level manufacturing example showing zones and conduits After determining the target SLs, the system can be designed (green field) or redesigned (brown field) to try to meet those target SLs. The design process is usually an iterative approach where the system design is checked against the target multiple times throughout the process. Multiple parts of the IEC 62443 series contain guidance on different aspects of the programmatic and technical requirements that go into the design process. IEC 62443‑2‑1 provides guidance on the programmatic aspects of the design process while IEC 62443‑3‑3 (this standard) and IEC 62443‑4‑2 [10] define system -level and component -level technical security requirements and relate them to different capability SLs. During the design process for a system, it is necessary to evaluate the security capabilities of different components and subsystems. Product suppliers will have to provide these as capability SLs for their components or systems by comparing features and capabilities with the requirements defined in the IEC 62443 series for the different capability SLs. These capability SLs can be used to determine whether a given component or system is capable of meeting the target SL for the system. The product supplier or syste m integrator will also have to provide guidance on how t o configure the component or system to meet the claimed SLs. It is likely that in a particular design there will be some components or systems that cannot fully meet the target SL. Where the capability SL of a component or system is lower than the target SL, compensating countermeasures need to be considered to meet the desired target SL. Compensating countermeasures may include changing the design of the component or system to increase its capabilities, choosing another component or system to meet the target SL or adding additional components or systems to meet the target SL. After each iteration in the design process, the system design’s achieved SLs should be reevaluated to see how they compare to th e target SLs for the system. Once the system design is approved and implemented, the system needs to be evaluated to prevent or mitigate deterioration of the system’s security level. It should be evaluated during or after system modifications and on a regu lar schedule. IEC 62443‑2‑1 provides guidance on the steps necessary to operate the security program and how to evaluate its effectiveness. After the achieved SLs have been determined, it will be necessary to evaluate whether the system is still meeting the original target SLs (for example, using the system requirements IEC 20 33/13 from IEC 62443‑3‑3). If the system is not meeting those requirements, there may be multiple reasons including the lack of maintenance of the program or the need to redesign parts of the system. In essence, the control system security capabilities are determined independent from a given use context, but are used in a given context in order to achieve the targ et SL of the respective system architecture, zones and/or conduits (see Figure A. 3). Figure A. 3 – Schematic of correlation of the use of different SL types A.3 SL vector A.3.1 Foundational requirements SLs are based on the seven FRs for security as defined in IEC 62443‑1‑1: 1) Identification and authentication control (IAC), 2) Use control (UC), 3) System integrity (SI), 4) Data confidentiality (DC), 5) Restrict ed data flow (RDF), 6) Timely response to event s (TRE), and 7) Resource availability (RA). IEC 2034/13 Instead of compressing SLs down to a single number, it is possible to use a vector of SLs that uses the seven FRs above instead of a single protection factor. This vector of SLs allows definable separations between SLs for the different FRs using language. This language can be based on the additional consequences associated with security systems or different attacks against the security objectives addressed by the FRs. The language used in the SL definitions can contain practical explanations of how one system is more secure than another without having to relate everything to HSE consequences. A.3.2 Level definitions A.3.2.1 Overview The IEC 62443 series define SLs in terms of five different levels (0, 1, 2, 3 and 4), each with an increasing level of security. The current model for defining SLs depends on protecting an increasingly more complex threat and differs slightly depending on what type of SL it is applied. For SL -C, this means that a particular component or system is capable of being configured by an as set owner or system integrator to protect against an increasingly complex type of threat. For SL- T, this means that the asset owner or system integrator has determined through a risk assessment that they need to protect this particular zone, system or component against this level of threat. For SL- A, this means that the asset owner, system integrator, product supplier and/or any combination of these has configured the zone, system or component to meet the particular security requirements defined for that SL. The language used for each of the SLs uses terms like casual, coincidental, simple, sophisticated and extended. This language is intentionally vague to allow the same basic language to be used for all of the documents in the IEC 62443 series. Each of the individual documents in the series will define the requirements for the SLs that apply to their particular purpose. While the requirements for each of the SLs will be different throughout the IEC 62443 series, there needs to be a general understanding of what each of the SLs should protect against. The following sections will provide some guidance on how to differentiate between the SLs. A.3.2.2 SL 0: No specific requirements or security protection necessary SL 0 has multiple meanings depending on the situation in which it is applied. In defining SL- C it would mean that the component or system fails to meet some of the SL 1 requirements for that particular FR. This would most li kely be for components or systems that would be part of a larger zone where other components or systems would provide compensating countermeasures. In defining SL- T for a particular zone it means that the asset owner has determined that the results of their risk analysis indicate that less than the full SL 1 specific requirements are necessary for that particular FR on that component or system. This would more likely happen for individual components within a system or zone that do not contribute in any way to the FR -specific requirements. In defining SL -A it would mean that the particular zone fails to meet some of the SL 1 requirements for that particular FR. A.3.2.3 SL 1: Protection against casual or coincidental violation Casual or coincidental violations of security are usually through the lax application of security polici es. These can be caused by well -meaning employees just as easily as they can be by an outsider threat. Many of these violations will be security program related and will be handled by enforcing policies and procedures. Using Figure A. 1, a simple example would be an operator able to change a set point on the engineering station in the BPCS zone to a value outside certain conditions determined by the engineering staff. The system did not enforce the proper authentication and use control restrictions to disallow the change by the operator. Also using Figure A. 1, another example would be a password being sent in clear text over the conduit between the BPCS zone and the DMZ zone, allowing a network engineer to view the password while troubleshooting the system. The system did not enforce proper data confidentiality to protect the password. Using Figure A. 2, a third example would be an engineer that means to access the PLC in Industrial Network #1 but actually accesses the PLC in Industrial Network #2. The system did not enforce the proper restriction of data flow preventing the engineer from accessing the wrong system. A.3.2.4 SL 2: Protection against intentional violation using simple means with low resources, generic skills and low motivation Simple means do no t require much knowledge on the part of the attacker. The attacker does not need detailed knowledge of security, the domain or the particular system under attack. These at tack vectors are well known and there may be automated tools for aiding the attacker. They are also designed to attack a wide range of systems instead of targeting a specific system, so an attacker does not need a significant level of motivation or resourc es at hand. Using Figure A. 1, an example would be a virus that infects the maintenance workstation in the Plant DMZ zone spreading to the BPCS engineering workstation since they both use the same general purpose operating system. Using Figure A. 2, another example would be an attacker compromising a web server in the enterprise network by an exploit downloaded from the Internet for a publicly known vulnerability in the general purpose operating system of the web server. The attacker uses the web server as a pivot point in an attack against other systems in the enterprise network as well as the industrial network. Also using Figure A. 2, a third example would be an operator that views a website on the HMI located in Industrial Network #1 which downloads a Trojan t hat opens a hole in the routers and firewalls to the Internet. A.3.2.5 SL 3: Protection against intentional violation using sophisticated means with moderate reso urces, IACS specific skills and moderate motivation Sophisticated means require advanced security knowledge, advanced domain knowledge, advanced knowledge of the target system or any combination of these. An attacker going after a SL 3 system will likely b e using attack vectors that have been customized for the specific target system. The attacker may use exploits in operating systems that are not well known, weaknesses in industrial protocols, specific information about a particular target to violate the security of the system or other means that require a greater motivation as well as skill and knowledge set than are required for SL 1 or 2. An example of sophisticated means could be password or key cracking tools based on hash tables. These tools are avail able for download, but applying them tak es knowledge of the system (such as the hash of a password to crack). Using Figure A. 1, another example would be an attacker t hat gains access to the FS-PLC through the serial conduit after gaining access to the control PLC through a vulnerability in the Ethernet controller. Using Figure A. 2, a third example would be an attacker that gains access to the data historian by using a bruteforce attack through the industrial/enterprise DMZ firewall initiated from the enterprise wireless network. A.3.2.6 SL 4: Protection against intentional violation using sophisticated means with extended resources, IACS specific skills and high motivation SL 3 and SL 4 are very similar in that they both involve sophisticated means used to violate the security requirements of the system. The difference comes from the attacker being even more motivated and having extended resources at their disposal. These may involve high-performance computing resour ces, large numbers of computers or extended periods of time. An example of sophisticated means with extended resources would be using super computers or computer clusters to conduct brute- force password cracking using large hash tables. Another example would be a botnet used to attack a system using multiple attack vectors at once. A third example would be an organized crime organization that has the motivation and resources to spend weeks attempting to analyze a system and develop custom “ zero -day” exploits. A.3.3 SL vector format A vector can be used to describe the security requirements for a zone, conduit, component or system b etter than a single number. This vector may contain either a specific SL requirement or a zero value for each of the foundational requirements (see A.3.1). FORMAT → SL -?([FR,]domain) = { IAC UC SI DC RDF TRE RA } where SL-? = (Required) The SL type (see A.2.2). The possible formats are: • SL-T = Target SL • SL-A = Achieved SL • SL-C = Capabilities SL [FR,] = (Optional) Field indicating the FR that the SL value applies. The FRs are written out in abbreviated form instead of numerical form to aid in readability. domain = (Required) The applicable domain that the SL applies. Domains can refer to zones, control systems, subsystems or components. Some examples of different domains from Figure A. 1 are SIS zone, BPCS zone, BPCS HMI, Plant DMZ domain controller, Plant DMZ to Control Center conduit and SIS to BPCS serial conduit. In this particular standard, all requirements refer to a control system, so the domain term is not used as it would be by ot her documents in the IEC 62443 series. EXAMPLE 1 → SL -T(BPCS Zone) = { 2 2 0 1 3 1 3 } EXAMPLE 2 → SL-C(SIS Engineering Workstation) = { 3 3 2 3 0 0 1 } EXAMPLE 3 → SL-C(RA, FS-PLC) = 4 NOTE The last example specifies only the RA component of a 7- dimension SL-C. Annex B (informative) Map ping of SRs and REs to FR SL levels 1-4 B.1 Overview This annex is intended to provide overall guidance to the reader as to how SL levels 0 to 4 are differentiated on an FR -by-FR basis via the defined SRs and their associated REs. B.2 SL mapping table Table B. 1 indicates which system level requirements apply to which FRs for a given sy stem capability SL – SL-C(xx, control system). For a given FR, the required system level requirements to meet a given SL- C are denoted by a check mark. Thus, as an example, the SL=1 system security capabilities for FR 5 (or SL-C(RDF, control system) =1), would include the base requirements of all four defined SRs. A system unable to meet all four of these SRs would have an SL -C(RDF, control system) =0. To meeting SL-C (RDF, control system) =2, a system needs to support the four SR base requirements plus RE(1) of SR 5. 1 and SR 5. 2. As another example, only the SR 6.1 base requirement is required to meet SL -C(TRE, control system) =1, but both SRs defined are required in order to meet SL-C (TRE, control system) =2. Refer to A.3.3 for how a full SL vector would be denoted. Table B.1 – Mapping of SRs and REs to FR SL levels 1 -4 (1 of 4) SRs and REs SL 1 SL 2 SL 3 SL 4 FR 1 – Identification and authentication control (IAC) SR 1.1 – Human user identification and authentication 5.3     SR 1.1 RE 1 – Unique identification and authentication 5.3.3.1    SR 1.1 RE 2 – Multifactor authentication for untrusted networks 5.3.3.2   SR 1.1 RE 3 – Multifactor authentication for all networks 5.3.3.3  SR 1.2 – Software process and device identification and authentication 5.4    SR 1.2 RE 1 – Unique identification and authentication 5.4.3.1   SR 1.3 – Account management 5.5     SR 1.3 RE 1 – Unified account management 5.5.3.1   SR 1.4 – Identifier management 5.6     SR 1.5 – Authenticator management 5.7     SR 1.5 RE 1 – Hardware security for software process identity credentials 5.7.3.1   SR 1.6 – Wireless access management 5.8     SR 1.6 RE 1 – Unique identification and authentication 5.8.3.1    SR 1.7 – Strength of password -based authentication 5.9     SR 1.7 RE 1 – Password generation and lifetime restrictions for human users 5.9.3.1   Table B. 1 (2 of 4) SRs and REs SL 1 SL 2 SL 3 SL 4 SR 1.7 RE 2 – Password lifetime restrictions for all users 5.9.3.2  SR 1.8 – Public key infrastructure certificates 5.10    SR 1.9 – Strength of public key authentication 5.11    SR 1.9 RE 1 – Hardware security for public key authentication 5.11.3.1   SR 1.10 – Authenticator feedback 5.12     SR 1.11 – Unsuccessful login attempts 5.13     SR 1.12 – System use notification 5.14     SR 1.13 – Access via untrusted networks 5.15     SR 1.13 RE 1 – Explicit access request approval 5.15.3.1    FR 2 – Use control (UC) SR 2.1 – Authorization enforcement 6.3     SR 2.1 RE 1 – Authorization enforcement for all users 6.3.3.1    SR 2.1 RE 2 – Permission mapping to roles 6.3.3.2    SR 2.1 RE 3 – Supervisor override 6.3.3.3   SR 2.1 RE 4 – Dual approval 6.3.3.4  SR 2.2 – Wireless use control 6.4     SR 2.2 RE 1 – Identify and report unauthorized wireless devices 6.4.3.1   SR 2.3 – Use control for portable and mobile devices 6.5     SR 2.3 RE 1 – Enforcement of security status of portable and mobile devices 6.5.3.1   SR 2.4 – Mobile code 6.6     SR 2.4 RE 1 – Mobile code integrity check 6.6.3.1   SR 2.5 – Session lock 6.7     SR 2.6 – Remote session termination 6.8    SR 2.7 – Concurrent session control 6.9   SR 2.8 – Auditable events 6.10     SR 2.8 RE 1 – Centrally managed, system -wide audit trail 6.10.3.1   SR 2.9 – Audit storage capacity 6.11     SR 2.9 RE 1 – Warn when audit record storage capacity threshold reached 6.11.3.1   SR 2.10 – Response to audit processing failures 6.12     SR 2.11 – Timestamps 6.13    SR 2.11 RE 1 – Internal time synchronization 6.13.3.1   SR 2.11 RE 2 – Protection of time source integrity 6.13.3.2  SR 2.12 – Non-repudiation 6.14   SR 2.12 RE 1 – Non-repudiation for all users 6.14.3.1  Table B.1 (3 of 4) SRs and REs SL 1 SL 2 SL 3 SL 4 FR 3 – System integrity (SI) SR 3.1 – Communication integrity 7.3     SR 3.1 RE 1 – Cryptographic integrity protection 7.3.3.1   SR 3.2 – Malicious code protection 7.4     SR 3.2 RE 1 – Malicious code protection on entry and exit points 7.4.3.1    SR 3.2 RE 2 – Central management and reporting for malicious code protection 7.4.3.2   SR 3.3 – Security functionality verification 7.5     SR 3.3 RE 1 – Automated mechanisms for security functionality verification 7.5.3.1   SR 3.3 RE 2 – Security functionality verification during normal operation 7.5.3.2  SR 3.4 – Software and information integrity 7.6    SR 3.4 RE 1 – Automated notification about integrity violations 7.6.3.1   SR 3.5 – Input validation 7.7     SR 3.6 – Deterministic output 7.8     SR 3.7 – Error handling 7.9    SR 3.8 – Session integrity 7.10    SR 3.8 RE 1 – Invalidation of session IDs after session termination 7.10.3.1   SR 3.8 RE 2 – Unique session ID generation 7.10.3.2   SR 3.8 RE 3 – Randomness of session IDs 7.10.3.3  SR 3.9 – Protection of audit information 7.11    SR 3.9 RE 1 – Audit records on write-once media 7.11.3.1  FR 4 – Data confidentiality (DC) SR 4.1 – Information confidentiality 8.3     SR 4.1 RE 1 – Protection of confidentiality at rest or in transit via untrusted networks 8.3.3.1    SR 4.1 RE 2 – Protection of confidentiality across zone boundaries 8.3.3.2  SR 4.2 – Information persistence 8.4    SR 4.2 RE 1 – Purging of shared memory resources 8.4.3.1   SR 4.3 – Use of cryptography 8.5     FR 5 – Restricted data flow (RDF) SR 5.1 – Network segmentation 9.3     SR 5.1 RE 1 – Physical network segmentation 9.3.3.1    SR 5.1 RE 2 – Independence from non-control system networks 9.3.3.2   SR 5.1 RE 3 – Logical and physical isolation of critical networks 9.3.3.3  Table B. 1 (4 of 4) SRs and REs SL 1 SL 2 SL 3 SL 4 SR 5.2 – Zone boundary protection 9.4     SR 5.2 RE 1 – Deny by default, allow by exception 9.4.3.1    SR 5.2 RE 2 – Island mode 9.4.3.2   SR 5.2 RE 3 – Fail close 9.4.3.3   SR 5.3 – General purpose person- to-person communication restrictions 9.5     SR 5.3 RE 1 – Prohibit all general purpose person - to-person communications 9.5.3.1   SR 5.4 – Application partitioning 9.6     FR 6 – Timely response to event s (TRE) SR 6.1 – Audit log accessibility 10.3     SR 6.1 RE 1 – Programmatic access to audit logs 10.3.3.1   SR 6.2 – Continuous monitoring 10.4    FR 7 – Resource availability (RA) SR 7.1 – Denial of service protection 11.3     SR 7.1 RE 1 – Manage communication loads 11.3.3.1    SR 7.1 RE 2 – Limit DoS effects to other systems or networks 11.3.3.2   SR 7.2 – Resource management 11.4     SR 7.3 – Control system backup 11.5     SR 7.3 RE 1 – Backup verification 11.5.3.1    SR 7.3 RE 2 – Backup automation 11.5.3.2   SR 7.4 – Control system recovery and reconstitution 11.6     SR 7.5 – Emergency power 11.7     SR 7.6 – Network and security configuration settings 11.8     SR 7.6 RE 1 – Machine- readable reporting of current security settings 11.8.3.1   SR 7.7 – Least functionality 11.9     SR 7.8 – Control system component inventory 11.10    Bibliography NOTE 1 This bibliography includes references to sources used in the creation of this standard as well as references to sources that may aid the reader in developing a greater understanding of cyber security as a whole and of the process of developing a cyber -security management system. Not all references in this bibliography are referred to throughout the text of this standard. The references have been grouped into different categories based on their source. References to other parts, both existing and in progres s, of the IEC 62443 series: NOTE 2 These references are not all published documents; some of them are in development. They are listed here for completeness of the currently authorized parts of the IEC 62443 series. [1] IEC/TR 62443‑1‑2, Industrial communication networks – Network and system security – Part 1-2: Master glossary of terms and abbreviations 3 [2] IEC/TS 62443‑1‑3, Indust rial communication networks – Network and system security – Part 1-3: System security compliance metrics 4 [3] IEC/TR 62443‑1‑4, Industrial communication networks – Network and system security – Part 1-4: IACS security lifecycle and use- case 5 [4] IEC/TR 62443‑2‑2, Industrial communication networks – Network and system security – Part 2-2: Implementation guidance for an IACS security management system 6 [5] IEC/TR 62443‑2‑3, Industrial communication networks – Network and system security – Part 2-3: Patch management in the IACS environment 7 [6] IEC 62443‑2‑4, Industrial communication networks – Network and system security – Part 2-4: Installation and maintenance requirements for IACS suppliers 8 [7] IEC/TR 62443‑3‑1, Industrial communication networks – Network and system security – Part 3-1: Security technologies for industrial automation and control systems [8] IEC 62443‑3‑2, Industrial communication networks – Network and system security – Part 3-2: Security levels for zones and conduits 9 [9] IEC 62443‑4‑1, Industrial communication networks – Network and system security – Part 4-1: Product development requirements 10 [10] IEC 62443‑4‑2, Industrial communication netwo rks – Network and system security – Part 4-2: Technical security requirements for IACS components 11 ___________ 3 Under consideration. 4 To be published. 5 Under consideration. 6 Under consideration. 7 Under consideration. 8 To be published. 9 Under consideration. 10 Under consideration. 11 Under consideration. Other standards references: [11] ISO/IEC Directives, Part 2:2011, Rules for the structure and drafting of International Standards [12] ISO/IEC 19790, Information techn ology – Security techniques – Security requirements for cryptographic modules [13] ISO/IEC 27002, Information technology – Security techniques – Code of practice for information security management [14] NERC CIP-002, Cyber Secu

## QA Summary
Metric | Count
Component base requirements | 69
Component enhancements | 45
System base requirements | 47
System enhancements | 44
Blank base requirement texts | 0
Blank base rationales | 0